## Intro
Project Number/Initials | 53100_Swansea Bay
Date started | 2024-08-05
Description of work undertaken | This calculation: -logs the incoming flow data quality checks -Holds a log of conversations with the flow survey contractor regarding data quality (financials not discussed here) -Records and compares dry days/storms to the WAPUG criteria -Carrys out a volume balance analysis of the flow monitors -contains process of analysing rainfall and logs adjustments made. This calculation ensures checks are completed that justify the removal/ending of the flow survey. This calculation needs to be undertaken alongside the Rainfall Assessment_V2 checksheet.

## Overview
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39
[6 empty] | Columns used to generate graph template |  |  |  | Enviromontel Performance Spreadsheet | [8 empty] | Arup Presite Spreadsheet |  |  | Install Checks |  |  |  |  | Flow Survey Contractor Interim Comments - take from relevant tab on Performance Tab
FM / DM / PL | Requester | Removal checker | Removal reviewer | Actioned | Removal Date | Observed Location | Predicted Location | Rainfall Profile | Upstream? | Install Date | W3W | Location | MH Reference | Pipe | Height (mm) | Width (mm) | Shape | Depth (mm) | MH Reference | Pipe | Position (inc/out) | Correct Location? | Correct Install Pipe? | Correct Pipe Size? | Correct Pipe Shape? | Comments | Interim 1 Notes | Interim 2 Notes | Interim 3 Notes | Interim 4 Notes | Interim 5 Notes | Interim 6 Notes | Interim 7 Notes | Interim 8 Notes | Interim 9 Notes | Interim 10 Notes | Interim 11 Notes | Interim 12 Notes
FM01 | JF |  |  | Removal Requested 19/09 |  |  | SN68018702.1 |  |  | 2024-07-18 | Estate.agreed.loved | Outside 56 heol eithrim SA6 5ES | SN68018803 | B | 150 | 150 | C | 1500 | SN68018803 | 225 | Incoming |  |  |  |  | https://arup.sharepoint.com/:x:/r/sites/SOAFStage3/Shared%20Documents/ECS/Swansea_FMInstallCheck.xlsx?d=w86e5ea08128a4813bfee8535ddf9e7b7&csf=1&web=1&e=EIUNGj | #REF! | #REF! | #REF! | #REF! | #REF! | Trickle flow. Sensor cleaned from ragging. Data downloaded | Data downloaded. Monitor removed | REMOVED | REMOVED | REMOVED | REMOVED
FM02 | JF |  |  | Removal Requested 19/09 |  |  | SN68018702.1 | [11 empty] | SN68017305 | 225 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Telemetry data downloaded | Data downloaded. Monitor removed | REMOVED | REMOVED | REMOVED | REMOVED
FM03 | [6 empty] | SN68019303.1 |  |  | 2024-07-30 | Backpacks.bicker.seasons | Outside 18 Sybil street, SA6 5EU | SN69010301 | B | 225 | 225 | C | 1740 | SN69010301 | 225 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Slow flow. Sensor cleaned from ragging. Graph showed calibration error - Sensor recalibrated. Data downloaded | Steady flow. Sensor cleaned from ragging. Data downloaded | Trickle flow. Sensor cleaned from ragging. Sensor recalibrated to match manual readings. Data downloaded | Steady flow. Sensor cleaned from ragging. Data downloaded | Slow flow. Sensor cleaned from ragging and grease. Data downloaded | Slow flow. Sensor cleaned from ragging and grease. Data downloaded
FM04 | [6 empty] | SN69010402.1 |  |  | 2024-07-19 | Rattler.purified.powerful | Outside 32 sybil street, SA6 5EX | SN69010403 | B | 525 | 525 | C | 1950 | SN69010403 | 375 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Steady flow. Sensor clear but wiped anyway. Data downloaded | Steady flow. Sensor cleaned from ragging. Data downloaded | Steady flow. Sensor cleaned from ragging. Data downloaded | Steady flow. Sensor cleaned from ragging. Data downloaded | Steady flow. Sensor cleaned from ragging and grease. Data downloaded | Steady flow. Sensor cleaned from ragging and grease. Data downloaded
FM05 | [6 empty] | SN69010402.2 |  |  | 2024-07-19 | Vaulting.scream.writing | Outside 32 sybil street, SA6 5EX | SN69010403 | B | 225 | 225 | C | 1500 | SN69010401 | 225 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Dry pipe. Sensor cleaned from ragging. Data downloaded | Trickle flow. Sensor cleaned from ragging. Data downloaded | Trickle flow. Sensor cleaned from ragging. Data downloaded | Trickle flow. Sensor cleaned from ragging. Data downloaded | Dry pipe - data downloaded | Dry pipe. Sensor clear but wiped anyway. Data downloaded
FM06 | JF |  |  | Removed and relocated to FM155 20/09 |  |  | STORM NETWORK NOT IN ICM |  |  | 2024-07-30 | Ledge.gong.acted | Heol y nant outside piccolo bar, SA6 5LG | SN69011308 SN69011311 (storm line) | A | 525 | 525 | C | 2850 | SN69011308 | 525 | Incoming - storm | No |  |  |  | Found to be installed in storm line, moved 20/09 to FM155 | #REF! | #REF! | #REF! | #REF! | #REF! | Steady flow. Data downloaded. Monitor removed and relocated. | Removed, relocated to FM155 | Removed, relocated to FM155 | Removed, relocated to FM155 | Removed, relocated to FM155 | Removed, relocated to FM155
FM07 | [9 empty] | Scrapped | [16 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Telemetry data downloaded | SCRAPPED | SCRAPPED | SCRAPPED | SCRAPPED | SCRAPPED
FM08 | [9 empty] | Scrapped | [16 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Telemetry data downloaded | SCRAPPED | SCRAPPED | SCRAPPED | SCRAPPED | SCRAPPED
FM09 | [6 empty] | SN69011203.1 |  |  | 2024-07-22 | Height.december.pest | Vale Clydach refinery, SA6 5QR | SN69011208 | X | 600 | 600 | C | 2950 | SN69011208 | 375 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Steady flow. Sensor cleaned from ragging. Data downloaded | Steady flow. Sensor clear but wiped anyway. Data downloaded | Fast flow. Sensor cleaned from ragging and grease. Data downloaded | Site visit required - unit does not dial in through the internet | Steady flow. Sensor cleaned from ragging and grease. Data downloaded | Steady flow. Sensor clear but wiped anyway. Data downloaded
FM10 | [6 empty] | SN68019201.1 |  |  | 2024-07-22 | Spreading.copiers.prepares | On canal side opposite bridge Street, SA6 5EJ | SN68019220 | B | 375 | 375 | C | 2150 | SN68019220 | 381 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Steady flow. Sensor cleaned from ragging. Data downloaded | Steady flow. Sensor clear but wiped anyway. Data downloaded | Steady flow. Sensor cleaned from ragging. Data downloaded | Steady flow. Sensor cleaned from ragging. Data downloaded | Steady flow. Sensor cleaned from ragging and grease. Data downloaded | Steady flow. Sensor clear but wiped anyway. Data downloaded
FM11 | [6 empty] | SN69011208.3 |  |  | 2024-07-22 | Puzzled.bidder.presides | Vale Clydach refinery, SA6 5QR | SN69011207 | A | 450 | 450 | C | 2300 | SN69011207 | 375 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Dry pipe. Sensor cleaned from grease. Data downloaded | Dry pipe. Sensor clear but wiped anyway. Data downloaded | Trickle flow. Sensor cleaned from debris. Data downloaded | Site visit required - unit does not dial in through the internet | Dry pipe. Sensor cleaned from ragging and grease. Data downloaded | Dry pipe. Sensor cleaned from debris. Data downloaded
FM12 | [9 empty] | Scrapped | [16 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Telemetry data downloaded | SCRAPPED | SCRAPPED | SCRAPPED | SCRAPPED | SCRAPPED
FM13 | [6 empty] | SN68018111.1 |  |  | 2024-07-15 | Universal.fires.pillows | On grass verge next to car, park beside 24 Hebron road SA6 5EJ | SN68019152 | A | 300 | 300 | C | 1880 | SN68019152 | 375 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Slow flow. Sensor cleaned from ragging. Data downloaded | Slow flow. Sensor cleaned from ragging. Data downloaded | Slow flow, pipe nearly at full bore. Sensor cleaned from ragging. Data downloaded | Slow flow. Sensor cleaned from ragging. Data downloaded | Slow flow. Sensor cleaned from ragging and grease. Data downloaded | Slow flow. Sensor cleaned from ragging and grease. Data downloaded
FM14 | [6 empty] | SN68018205.1 |  |  | 2024-07-30 | Beanbag.curl.logged | Outside 27 Hebron rd | SN68018148 | B | 300 | 300 | C | 1930 | SN68018148 | 375 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Slow flow. Sensor cleaned from ragging. Data downloaded | Steady flow. Sensor cleaned from ragging. Data downloaded | Site visit required - unit does not dial in through the internet | Trickle flow. Sensor cleaned from ragging. Data downloaded | Slow flow. Sensor cleaned from ragging and grease. Data downloaded | Slow flow. Sensor cleaned from ragging and grease. Data downloaded
FM15 | [6 empty] | SN68018206.1 |  |  | 2024-07-30 | Currently.commander.pines | Outside 3 Quarr Rd, SA6 5BY | SN68018202 | B | 225 | 225 | C | 1350 | SN68018202 | 225 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Steady flow. Sensor cleaned from ragging. Data downloaded | Site visit required - unit does not dial in through the internet | Unable to access. Parked cars blocking room for setup | Steady flow. Sensor cleaned from ragging. Data downloaded | Steady flow. Sensor cleaned from ragging and grease. Data downloaded | Steady flow. Sensor cleaned from ragging and grease. Data downloaded
FM16 | [6 empty] | SN68017209.1 |  |  | 2024-07-25 | Taken.important.storming | On quarr road at the back of 2 aberclydach place | SN68017211 | A | 225 | 225 | C | 1700 | SN68017211 | 225 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Steady flow. Sensor cleaned from ragging. Sensor recalibrated to match manual measurements. Data downloaded | Fast flow. Sensor clear but wiped anyway. Data downloaded | Steady flow. Sensor cleaned from grease. Data downloaded | Steady flow. Sensor cleaned from ragging. Data downloaded | Steady flow. Sensor cleaned from ragging and grease. Data downloaded | Steady flow. Sensor cleaned from ragging and grease. Data downloaded
FM17 | [6 empty] | SN70003802.1 |  |  | 2024-07-30 | Fool.attending.wash | Outside Chapel sion, SA7 9JA | SN70003802 | A | 375 | 375 | C | 1800 | SN70003802 | 375 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Site visit required - unit does not dial in through the internet | Telemetry data downloaded | Data downloaded. Monitor removed | REMOVED | REMOVED | REMOVED
FM18 | [6 empty] | SN70003805.1 - SHOULD BE SPILL LINK?? |  |  | 2024-07-30 | Organisms.suspend.taster | Ynys y Mond rd Junction of bridge Street, SA6 5LE | SN70002705 | Y | 300 | 300 | C | 1630 | SN70002705 | 300 | Outgoing (Spill Pipe) | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Site visit required - unit does not dial in through the internet | Manhole surcharged - data downloaded. | Telemetry data downloaded | Site visit required - unit does not dial in through the internet |  | REMOVED
FM19 | JF |  |  | Removal Requested 19/09 |  |  | SN68002308.1 |  |  | 2024-07-30 | Scores.helpless.listening | Clydach rd Junction to school | SN68002307 | X | 300 | 300 | C | 5440 | SN68002308 | 225/300 | Outgoing | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Steady flow. Sensor cleaned from grease. Data downloaded | Data downloaded. Monitor removed | REMOVED | REMOVED | REMOVED | REMOVED
FM20 | JF |  |  | Removal Requested 19/09 |  |  | SN68003201_Dummy.1 |  |  | 2024-07-19 | Intervals.rocky.severe | Beside gas governor, ynystawe, clydach, SA6 5BQ | SN68003201 | Y | 300 | 300 | C | 5730 | SN68003201 | 300 | Outgoing (Spill Pipe) | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Dry pipe. Sensor wiped and recalibrated. Data downloaded | Data downloaded. Monitor removed | REMOVED | REMOVED | REMOVED | REMOVED
FM21 | [6 empty] | MH1-73413.2 |  |  | 2024-07-15 | Lighters.snails.keyboards | Grass verge just off the roundabout, SA6 6QJ | SS67996308 | A | 675 | 675 | C | 4380 | SS67996308 | 675 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Steady flow. Sensor cleaned from ragging. Data downloaded | Steady flow. Sensor clear but wiped anyway. Data downloaded | Data downloaded. Monitor removed | REMOVED | REMOVED | REMOVED
FM22 | JF |  |  | Removal Requested 19/09 |  |  | MH1-73413.1 |  |  | 2024-07-29 | Firewall.poets.woodstove | In car park area | SS67996309 | A | 450 | 450 | C | 3700 | SS67996309 | 675 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Unable to enter. Parked car on manhole. Note left on car | Data downloaded. Monitor removed | REMOVED | REMOVED | REMOVED | REMOVED
FM23 | [6 empty] | SS67999701.1 |  |  | 2024-07-31 | natively.surging.liquid | Near 461-481 Clydach Rd, Ynysforgan, Swansea SA6 6QW | SS67998601 | X | 600 | 600 | C | 4500 | SS67998601 | 868 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Steady flow. Sensor cleaned from ragging. Data downloaded | Steady flow. Sensor cleaned from ragging. Sensor calibrated to match manual measurements. Data downloaded | Site visit required - unit does not dial in through the internet | Steady flow. Sensor cleaned from ragging. Data downloaded | Steady flow. Sensor cleaned from ragging and grease. Data downloaded | Steady flow. Sensor cleaned from ragging and grease. Data downloaded
FM24 | JF |  |  | Removal Requested 19/09 |  |  | SS70980301.1 |  |  | 2024-07-15 | Later.shelving.tones | On path of heol dulais, SA7 9LT | SS70980314 | A | 225 | 225 | C | 2040 | SS70980314 | 225 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Steady flow. Sensor cleaned from ragging. Data downloaded | Data downloaded. Monitor removed | REMOVED | REMOVED | REMOVED | REMOVED
FM25 | JF |  |  | Removal Requested 19/09 |  |  | MH07.1 |  |  | 2024-07-30 | Colder.diverged.then | Near Parc Bedw, Birchgrove, Swansea SA7 9LU | SS70980312 | X | 225 | 225 | C | 1970 | SS70980312 | 225 | Outgoing | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Steady flow. Sensor and cable cleaned thoroughly from heavy ragging and grease. Data downloaded | Data downloaded. Monitor removed | REMOVED | REMOVED | REMOVED | REMOVED
FM26 | JF |  |  | Removal Requested 19/09 |  |  | SS70980404.1 |  |  | 2024-07-15 | Juicy.softly.jumps | Gravel track on heol dulais, SA7 9DX | SS69989525 | A | 225 | 225 | C | 2460 | SS69989525 | 225 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Telemetry data downloaded | Data downloaded. Monitor removed | REMOVED | REMOVED | REMOVED | REMOVED
FM27 | [6 empty] | SN70000705.1 |  |  | 2024-07-15 | Clips.cocoons.played | Field of 1 wern y glais cottages SA7 9ES | SN70000760 | A | 225 | 225 | C | 1825 | SN70000760 - unplotted | 225 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Site visit required - unit does not dial in through the internet | Steady flow. Sensor cleaned from ragging. Data downloaded | Data downloaded. Monitor removed | REMOVED | REMOVED | REMOVED
FM28 | JF |  |  | Removal Requested 19/09 |  |  | SS69985401.1 |  |  | 2024-07-19 | Modifies.faced.optimally | Outside 345 Heollas Close, SA7 9DP | SS69984401 | A | 300 | 300 | C | 2570 | SS69984401 | 300 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Steady flow. Sensor cleaned from ragging and grease. Data downloaded | Data downloaded. Monitor removed | REMOVED | REMOVED | REMOVED | REMOVED
FM29 | [6 empty] | SS69982401_dum.1 |  |  | 2024-07-30 | Consonant.feasting.stutter | On corner of heol Las Road, corner house, SA7 9DZ | SS69982507 | A | 375 | 375 | C | 1900 | SS69982507 | 375 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Telemetry data downloaded | Telemetry data downloaded | Steady flow. Sensor cleaned from grease. Data downloaded | Steady flow. Sensor cleaned from ragging. Data downloaded | Steady flow. Sensor cleaned from ragging and grease. Data downloaded | Steady flow. Sensor cleaned from ragging and grease. Data downloaded
FM30 | [6 empty] | SN70000603.1 |  | YES | 2024-07-31 | Hardening.pranced.pausing | Outside no 54 Station Rd, SA7 9HE | SN70000603 | X | 600 | 600 | C | 4160 | SN70000603 | 600 | Outgoing | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Site visit required - unit does not dial in through the internet | Steady flow. Sensor clear but wiped anyway. Data downloaded | Data downloaded. Monitor removed | REMOVED | REMOVED | REMOVED
FM31 | [6 empty] | SS66998101.1 |  |  | 2024-07-18 | Supporter.slower.breath | Outside 5 cwmrhydyceirw, SA6 6TH | SS66997101 | A | 225 | 225 | C | 1090 | SS66997101 | 225 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Slow flow. Sensor cleaned from ragging. Data downloaded | Steady flow. Sensor clear but wiped anyway. Data downloaded | Steady flow. Sensor cleaned from ragging and grease. Data downloaded | Steady flow. Sensor cleaned from ragging and grease. Data downloaded | Data downloaded. Monitor removed | REMOVED
FM32 | JF |  |  | Removed and relocated to FM156 03/09 |  |  | SS66987901.1 |  | YES | 2024-07-18 | Mug.swung.member | Outside 7 heol dyfan, vicarage road, SA6 6DX | SS66997004 | A | 225 | 225 | C | 1750 | SS66997004 | 225 | Outgoing |  |  |  |  | Installed incorrectly on incoming pipe, moved to outgoing pipe 03/09 to FM156 | #REF! | #REF! | #REF! | #REF! | #REF! | Steady flow. Sensor cleaned from ragging and grease. Sensor pushed further into the pipe. Data downloaded | Removed, relocated to FM156 | Removed, relocated to FM156 | Removed, relocated to FM156 | Removed, relocated to FM156 | REMOVED
FM33 | [6 empty] | SS66997005.1 - SHOULD BE SPILL LINK?? |  |  | 2024-07-18 | Delay.luck.points | On bend of 7 Heol Dyfan, Morriston, Swansea SA6 6DY near centre of road | SS66997002 | Y | 150 | 150 | C | 2540 | SS66997002 | 150 | Outgoing (Spill Pipe) | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Dry pipe. Sensor clear but wiped anyway. Sensor offset 3mm prevent negative readings. Data downloaded | Site visit required - unit does not dial in through the internet | Dry pipe. Sensor clear but wiped anyway. Data downloaded | Dry pipe. Sensor clear but wiped anyway. Data downloaded | Data downloaded. Monitor removed | REMOVED
FM34 | JF |  |  | Removed and relocated to FM157 19/09 |  |  | SS66989208.1 |  | YES | 2024-07-24 | Breed.topped.simply | Outside 96 pleasant street, SA6 6HJ | SS66989207 | C | 300 | 300 | C | 3000 | SH66989207 | 300 | Incoming |  |  |  |  | Relocated on 19/09 to FM157 | #REF! | #REF! | #REF! | #REF! | #REF! | Fast flow - Jumping the sensor. Data downloaded. Monitor removed and relocated | Removed, relocated to FM157 | Removed, relocated to FM157 | Removed, relocated to FM157 | Removed, relocated to FM157 | Removed, relocated to FM157
FM35 | JF |  |  | Removed and relocated to FM158 10/09 |  |  | SS66989301.1 |  |  | 2024-07-17 | Echo.shin.loads | Outside 31 pentrepoeth Road in parking bay SA6 6HJ | SS66989301 | A | 300 | 300 | C | 3550 | SH66989301 | 450 | Incoming |  |  |  |  | Relocated to X pipe on 10/09 to FM158 | #REF! | #REF! | #REF! | #REF! | #REF! | Fast flow. Sensor cleaned from ragging. Data downloaded | Removed, relocated to FM158 | Removed, relocated to FM158 | Removed, relocated to FM158 | Removed, relocated to FM158 | Removed, relocated to FM158
FM36 | [9 empty] | Scrapped | [16 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Telemetry data downloaded | SCRAPPED | SCRAPPED | SCRAPPED | SCRAPPED | SCRAPPED
FM37 | [6 empty] | SS69964102.1 |  |  | 2024-07-17 | Angle.pace.brand | In field to right of sps, SA7 9XR | SS69964108 | X | 900 | 900 | C | 5000 | SS69964108 | 900 | Outgoing | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Steady flow. Sensor cleaned of ragging. Data downloaded | Steady flow. Sensor clear but wiped anyway. Data downloaded | Data downloaded. Monitor removed | REMOVED | REMOVED | REMOVED
FM38 | JF |  |  | Removal Requested 19/09 |  |  | SS69974101.1 |  |  | 2024-07-30 | Coach.drag.moss | Near Llansamlet, Swansea | SS69974101 | X | 400 | 400 | C | 2470 | SS69974101 | 300 | Outgoing | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Steady flow. Sensor cleaned from ragging and grease. Data downloaded | Data downloaded. Monitor removed | REMOVED | REMOVED | REMOVED | REMOVED
FM39 | JF |  |  | Removal Requested 19/09 |  |  | SS69974302.1 |  |  | 2024-07-29 | Exact.souk.remind | On road outside church | SS69973302 | A | 375 | 375 | C | 2400 | SS69973302 | 375 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Steady flow. Sensor cleaned from ragging and grease. Data downloaded | Data downloaded. Monitor removed | REMOVED | REMOVED | REMOVED | REMOVED
FM40 | JF |  |  | Removal Requested 19/09 |  |  | SS69973303.1 |  |  | 2024-07-30 | Heap.comical.grows | Outside 19 Bethel Road | SS69972304 | A | 750 | 750 | C | 3370 | SS69972304 | 750 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Steady flow. Sensor cleaned from ragging and grease. Data downloaded | Data downloaded. Monitor removed | REMOVED | REMOVED | REMOVED | REMOVED
FM41 | JF |  |  | Removal Requested 19/09 |  |  | SS69972303.1 |  |  | 2024-07-30 | Heap.comical.grows | Outside 19 Bethel Road | SS69972304 | B | 300 | 300 | C | 3370 | SS69972304 | 375 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Steady flow. Sensor cleaned from ragging and grease. Data downloaded | Data downloaded. Monitor removed | REMOVED | REMOVED | REMOVED | REMOVED
FM42 | JF |  |  | Removal Requested 19/09 |  |  | SS69974501.1 |  |  | 2024-07-31 | Budget.expert.bench | Outside 141 peniel green rd, SA7 9BD | SS68872501 | A | 400 | 400 | C | 2670 | SS68872501 | 450 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Steady flow. Sensor cleaned from grease. Data downloaded | Data downloaded. Monitor removed | REMOVED | REMOVED | REMOVED | REMOVED
FM43 | JF |  |  | Removal Requested 19/09 |  |  | SS69972409.1 |  |  | 2024-07-31 | Labs.awards.nodded | Side of peniel green Rd Opposite FMC limited, SA7 9BA | SS69972502 | B | 525 | 525 | C | 2530 | SS69972503 | 600 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Steady flow. Sensor cleaned from ragging. Data downloaded | Data downloaded. Monitor removed | REMOVED | REMOVED | REMOVED | REMOVED
FM44 | JF |  |  | Removal Requested 19/09 |  |  | SS68974501.1 |  |  | 2024-08-02 | Deal.harsh.fell | Llansamlet, SA7 9AF | SS68972507 | A | 700 | 700 | C | 3160 | SS68972507 | 825 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Steady flow. Sensor cleaned from ragging and grease. Data downloaded | Data downloaded. Monitor removed | REMOVED | REMOVED | REMOVED | REMOVED
FM45 | [6 empty] | SS68972508_orfice.1 |  |  | 2024-07-18 | Spared.slime.stacks | Central reservation opposite tile and bath, SA7 9AF | SS68972506 | A | 450 | 450 | C | 3050 | SS68972506 | 375 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Telemetry data downloaded | Telemetry data downloaded | Telemetry data downloaded | Steady flow. Sensor cleaned from ragging. Data downloaded | Steady flow. Sensor clear but wiped anyway. Data downloaded | Steady flow. Sensor clear but wiped anyway. Data downloaded
FM46 | [9 empty] | Scrapped | [16 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Telemetry data downloaded | SCRAPPED | SCRAPPED | SCRAPPED | SCRAPPED | SCRAPPED
FM47 | JF |  |  | Removal Requested 19/09 |  |  | SS67970703.1 |  |  | 2024-07-18 | Suffice.bricks.spoon | On corner of clos-camlas, SA6 8EP | SS67971705 | B | 475 | 475 | C | 2950 | SS67971705 | 500 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Slow flow. Sensor cleaned from ragging. Data downloaded | Data downloaded. Monitor removed | REMOVED | REMOVED | REMOVED | REMOVED
FM48 | [6 empty] | SS64924802.1 |  |  |  | Stops.bother.twist | Outside no 10 Westbury street, SA1 4JN | SS64924710 | A | 300 | 300 | C | 2830 | SS64924710 | 300 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Dry pipe. Sensor cleaned from grease. Data downloaded | Telemetry data downloaded | Telemetry data downloaded | Data downloaded. Monitor removed | Telemetry data downloaded
FM49 | [6 empty] | SS67971506.1 |  |  | 2024-07-18 | Farmer.grant.ally | On grass verge next to foot bridge, off on neath road, SA6 8DB | SS67971509 | A | 475 | 475 | C | 3460 | SS67971509 | 457 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Fast flow. Sensor cleaned from ragging. Sensor recalibrated to math manual measurements. Data downloaded | Steady flow. Sensor clear but wiped anyway. Data downloaded | Telemetry data downloaded | Fast flow. Sensor cleaned from ragging. Data downloaded | Fast flow. Sensor clear but wiped anyway. Data downloaded | Fast flow. Sensor clear but wiped anyway. Data downloaded
FM50 | JF |  |  | Removal Requested 19/09 |  |  | SS67978301.1 |  | YES | 2024-07-31 | Hero.grant.thick | Near Llansamlet, SA6 8WB | SS67978360 | X | 1000 | 1000 | C | 8750 | SS67978305 | 1200 | Outgoing | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Telemetry data downloaded | Data downloaded. Monitor removed | REMOVED | REMOVED | REMOVED | REMOVED
FM51 | [6 empty] | SS67971405.1 |  |  | 2024-07-17 | Manage.harder.hired | Edge of car park outside 69 wychtree street, SA6 8EY | SS67971302 | A | 900 | 900 | C | 7100 | SS67971302 | 900 x 711 brick egg | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Steady flow. Sensor cleaned from ragging and grease. Data downloaded | Steady flow. Sensor clear but wiped anyway. Data downloaded | Telemetry data downloaded | Steady flow. Sensor clear but wiped anyway. Data downloaded | Steady flow. Sensor cleaned from ragging and grease. Data downloaded | Steady flow. Sensor cleaned from ragging and grease. Data downloaded
FM52 | [9 empty] | Scrapped | [16 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Telemetry data downloaded | SCRAPPED | SCRAPPED | SCRAPPED | SCRAPPED | SCRAPPED
FM53 | [9 empty] | Scrapped | [16 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Telemetry data downloaded | SCRAPPED | SCRAPPED | SCRAPPED | SCRAPPED | SCRAPPED
FM54 | [6 empty] | SS64924702.2 |  |  | 2024-07-23 | Oiled.glee.epic | Westbury Street Outside no 2, SA1 4JN | SS64924703 | Y | 300 | 300 | C | 2950 | SS64924703 | 300 | Outgoing (Spill Pipe) | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Dry pipe. Sensor clear but wiped anyway. Data downloaded | Dry pipe. Sensor clear but wiped anyway. Data downloaded | Telemetry data downloaded | Data downloaded. Monitor removed | REMOVED | REMOVED
FM55 | JF |  |  | Removal Requested 19/09 |  |  | SS65975404.1 |  |  | 2024-07-17 | Cities.mime.mice | Outside the front of 3 Mynydd Garnllwyd Road, Morriston, Swansea SA6 7PB | SS65974401 | A | 225 | 225 | C | 2420 | SS65974401 | 225 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Steady flow. Sensor cleaned from ragging and grease. Data downloaded | Data downloaded. Monitor removed | REMOVED | REMOVED | REMOVED | REMOVED
FM56 | JF |  |  | Removal Requested 19/09 |  |  | SS65973402.1 |  | YES | 2024-07-16 | Shadow.arts.over | In park behing Gold tyres & Gold hand Car wash, Mynydd Garnllwyd Road, Moriston, Morriston, Swansea SA6 7PF | SS65973403 | A | 400 | 400 | C | 2450 | SS65973403 | 375 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Steady flow. Sensor cleaned from ragging. Data downloaded | Data downloaded. Monitor removed | REMOVED | REMOVED | REMOVED | REMOVED
FM57 | JF |  |  | Removal Requested 19/09 |  |  | SS65973201.1 |  | YES | 2024-07-18 | Matter.term.reveal | Junction of bryngelli park, SA5 9BW | SS65973202 | X | 300 | 300 | C | 1590 | SS65973202 | 300 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Telemetry data downloaded | Data downloaded. Monitor removed | REMOVED | REMOVED | REMOVED | REMOVED
FM58 | JF |  |  | Removal Requested 19/09 |  |  | SS65962901.2 |  |  | 2024-07-16 | Song.drama.unions | On corner of heol gerrig, SA5 9BP | SS65962903 | A | 225 | 225 | C | 980 | SS65962903 | 300 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Trickle flow. Sensor cleaned from ragging. Data downloaded | Data downloaded. Monitor removed | REMOVED | REMOVED | REMOVED | REMOVED
FM59 | [6 empty] | SS65962701.1 |  |  | 2024-07-25 | Bond.sage.castle | Outside 734 llangyfelach road | SS65962701 | A | 375 | 375 | C | 2600 | SS65962701 | 375 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Fast flow. Sensor cleaned from ragging and grease. Data downloaded | Telemetry data downloaded | Data downloaded. Monitor removed | REMOVED | REMOVED | REMOVED
FM60 | [6 empty] | SS65960602_DU.1 |  |  | 2024-07-25 | Finely.preoccupied.cape | Corner of penlan terrace | SS65960602 | A | 450 | 450 | C | 2800 | SS65960602 | 229 | Incoming (Storm) | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Steady flow. Sensor cleaned from grease. Data downloaded | Trickle flow. Sensor clear but wiped anyway. Data downloaded | Data downloaded. Monitor removed | REMOVED | REMOVED | REMOVED
FM61 | JF |  |  | Removal Requested 19/09 |  |  | SS65960502.1 |  |  | 2024-07-29 | Bottle.rocket.bikes | On hill on road outside 45 | SS65960503 | A | 325 | 325 | C | 2100 | SS65960503 | 305 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Data downloaded. Monitor removed | REMOVED | REMOVED | REMOVED | REMOVED | REMOVED
FM62 | JF |  |  | Removal Requested 19/09 |  |  | SS65966205.1 |  | YES | 2024-07-31 | Factories.filer.fourm | Near 25 Heol Nant Gelli, Tre-boeth, Swansea SA5 9DU | SS65966101 | Y | 375 | 375 | C | 2480 | SS65966201 | 229 | Outgoing (Spill Pipe) | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Trickle flow. Sensor clear but wiped anyway. Data downloaded | Data downloaded. Monitor removed | REMOVED | REMOVED | REMOVED | REMOVED
FM63 | JF |  |  | Removal Requested 19/09 |  |  | SS65966203.1 |  |  | 2024-07-17 | Pads.shout.perky | Near 25 Heol Nant Gelli, Treboeth, Swansea SA5 9DU | SS65966101 | A | 300 | 300 | C | 955 | SS65966101 | 300 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Steady flow. Sensor cleaned from ragging and grease. Data downloaded | Data downloaded. Monitor removed | REMOVED | REMOVED | REMOVED | REMOVED
FM64 | JF |  |  | Removal Requested 19/09 |  |  | SS65969201.1 |  |  | 2024-07-31 | Deputy.glass.trunk | Near 88 Trewyddfa Rd, Plasmarl, Swansea SA6 8NY | 9202 | A | 300 | 300 | C | 3650 | SS65969202 | 300 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Steady flow. Sensor cleaned from ragging and grease. Data downloaded | Data downloaded. Monitor removed | REMOVED | REMOVED | REMOVED | REMOVED
FM65 | [6 empty] | SS65966004.1 |  |  | 2024-08-01 | Stale.cried.wings | Near Plasmarl | SS65966003 | B | 400 | 400 | C | 2450 | SS65966003 | 450 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Site visit required - unit does not dial in through the internet | Data downloaded. Monitor removed | REMOVED | Fast flow. Sensor clear but wiped anyway. Data downloaded | Fast flow. Sensor cleaned from ragging and grease. Data downloaded | Fast flow. Sensor cleaned from ragging and grease. Data downloaded
FM66 | JF |  |  | Removal Requested 19/09 |  |  | SS65966001.1 |  |  | 2024-07-24 | Allow.meal.pulled | Cwm level road, outside no 85, SA6 8NJ | SS65966005 | A | 300 | 300 | C | 2550 | SS65966005 | 450 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Steady flow. Sensor cleaned from ragging. Data downloaded | Data downloaded. Monitor removed | REMOVED | REMOVED | REMOVED | REMOVED
FM67 | JF |  |  | Removed and relocated to FM159 10/09 |  |  | SS66951904.1 |  |  | 2024-07-31 | Using.case.blame | Near Plasmarl, SA6 8JT | SS66951970 | A | 800 | 800 | C | 6750 | SS66951970 | 750 | Incoming |  |  |  |  | Relocated to X pipe on 10/09 to FM159 | #REF! | #REF! | #REF! | #REF! | #REF! | Steady flow. Sensor cleaned from ragging and grease. Data downloaded | Removed, relocated to FM159 | Removed, relocated to FM159 | Removed, relocated to FM159 | REMOVED | REMOVED
FM68 | JF |  |  | Removal Requested 19/09 |  |  | SS66950703.1 |  |  | 2024-07-24 | Waddled.voting.still | Siloh road, before junction, SA1 2JG | SS66950702 | A | 450 | 450 | C | 2100 | SS66950702 | 450 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Telemetry data downloaded | Data downloaded. Monitor removed | REMOVED | REMOVED | REMOVED | REMOVED
FM69 | JF |  |  | Removal Requested 19/09 |  |  | SS66951709.1 |  |  | 2024-07-17 | Tight.search.candle | Swansea stadium North car park, bay 97, SA1 2FA | SS66951708 | A | 975 | 975 | C | 4750 | SS66951708 | 1000 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Standing water. Sensor cleaned from ragging. Data downloaded | Data downloaded. Monitor removed | REMOVED | REMOVED | REMOVED | REMOVED
FM70 | JF |  |  | Removed and relocated to FM160 10/09 |  |  | SS65954810.1 |  |  | 2024-07-22 | Saying.bells.remote | On grass behind bus stop, SA5 9EA | SS65954813 | B | 450 | 450 | C | 3300 | SS65954813 | 600 | Incoming |  |  |  |  | Relocated to X pipe on 10/09 to FM160 | #REF! | #REF! | #REF! | #REF! | #REF! | Fast turbulent flow. Sensor cleaned from ragging. Data downloaded | Removed, relocated to FM160 | Removed, relocated to FM160 | Removed, relocated to FM160 | Removed, relocated to FM160 | Removed, relocated to FM160
FM71 | [6 empty] | SS65954808.1 |  |  | 2024-07-17 | Pinch.unity.moment | On grass in car park of 499 Llangyfelach Rd, Brynhyfryd, Swansea SA5 9EB | SS65954814 | A | 600 | 600 | C | 4100 | SS65954814 | 600 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Steady flow. Sensor cleaned from ragging. Data downloaded | Steady flow. Sensor clear but wiped anyway. Data downloaded | Telemetry data downloaded | Steady flow. Sensor cleaned from ragging. Data downloaded | Fast flow. Unable to make entry to clean sensor, due to parked car. Data downloaded | Steady flow. Sensor clear but wiped anyway. Data downloaded
FM72 | [6 empty] | NO NETWORK |  |  | 2024-07-17 | Start.drips.ruins | Across from houses 4 and 5, on the pavement of Cwm level road, SA5 9DY | SS65955802 | A | 450 | 450 | C | 2490 | SS65955802 | 450 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Dry pipe. Sensor cleaned from ragging and grease. Data downloaded | Trickle flow. Sensor clear but wiped anyway. Data downloaded | Site visit required - unit does not dial in through the internet | Slow flow. Sensor cleaned from grease. Data downloaded | Trickle flow. Sensor cleaned from ragging and grease. Data downloaded | Slow flow. Sensor cleaned from ragging and grease. Data downloaded
FM73 | [6 empty] | SS65954811.1 |  |  | 2024-07-18 | Lasted.worth.shop | On pavement by bus stop opposite 494 Llangyfelach Rd, Brynhyfryd, Swansea SA5 9EA | SS65954811 | A | 900 | 900 | C | 4280 | SS65954811 | 900 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Steady flow. Sensor cleaned from ragging. Data downloaded | Steady flow. Sensor cleaned from ragging. Data downloaded | Telemetry data downloaded | Steady flow. Sensor cleaned from ragging. Data downloaded | Steady flow. Sensor cleaned from ragging and grease. Data downloaded | Steady flow. Sensor cleaned from ragging and grease. Data downloaded
FM74 | [6 empty] | SS65954710.1 |  |  | 2024-07-24 | Round.chips.brush | Outside of number 96 Eaton Road, SA5 9JH | SS65944707 | A | 480 | 480 | C | 2300 | SS65954707 | 450 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Telemetry data downloaded | Telemetry data downloaded | Unable to access. Parked cars blocking room for setup | Unable to access due to parked cars | Data downloaded. Monitor removed | REMOVED
FM75 | [6 empty] | SS65954303.1 |  |  | 2024-07-17 | Zooms.glory.wide | Clare St next to one stop, SA5 9JU | SS65954304 | X | 300 | 300 | C | 2600 | SS65954304 | 300 | Outgoing | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Steady flow. Sensor cleaned from ragging. Data downloaded | Steady flow. Sensor cleaned from ragging and grease. Data downloaded | Data downloaded. Monitor removed | REMOVED | REMOVED | REMOVED
FM76 | [6 empty] | SS65954402.1 |  |  | 2024-07-18 | Limit.solid.tapes | Eaton rd. Junction of Frederick street, SA5 9JL | SS65954412 | A | 450 | 450 | C | 3510 | SS65954412 | 450 | Outgoing | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Telemetry data downloaded | Telemetry data downloaded | Data downloaded. Monitor removed | REMOVED | REMOVED | REMOVED
FM77 | [6 empty] | SS65954403.1 |  |  | 2024-07-18 | Chairs.bride.neck | Eaton rd Junction of pleasant row, SA5 9JU | SS65954310 | A | 450 | 450 | C | 3780 | SS65954310 | 450 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Steady flow. Sensor cleaned from ragging and grease. Data downloaded | Steady flow. Sensor cleaned from ragging. Data downloaded | Steady flow. Sensor cleaned from ragging and grease. Data downloaded | Steady flow. Sensor cleaned from ragging and grease. Data downloaded | Steady flow. Sensor cleaned from ragging and grease. Data downloaded | Steady flow. Sensor cleaned from ragging and grease. Data downloaded
FM78 | JF |  |  | Removal Requested 19/09 |  |  | SS67955102.1 |  | YES | 2024-07-19 | Giant.sing.runs | Talfan Road junction, SA1 7AR | SS67955102 | X | 450 | 450 | C | 2245 | SS67955102 | 525 | Outgoing | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Telemetry data downloaded | Data downloaded. Monitor removed | REMOVED | REMOVED | REMOVED | REMOVED
FM79 | [9 empty] | Scrapped | [16 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Telemetry data downloaded | SCRAPPED | SCRAPPED | SCRAPPED | SCRAPPED | SCRAPPED
FM80 | JF |  |  | Removal Requested 19/09 |  |  | SS67952102A.1 |  |  | 2024-07-19 | Scuba.salads.bids | Bon y maen Road. At junction to school, SA1 7AP | SS67951201 | A | 400 | 400 | C | 3230 | SS67951201 | 375 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Telemetry data downloaded | Data downloaded. Monitor removed | REMOVED | REMOVED | REMOVED | REMOVED
FM81 | JF |  |  | Removal Requested 19/09 |  |  | SS66957003.1 |  | YES | 2024-08-06 | Bolt.voting.money | Near B5444, Bon-y-maen, SA1 7AA | SS66956001 | X | 450 | 450 | C | 4540 | SS66956001 | 525 | Outgoing | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Steady flow. Sensor cleaned from ragging and grease. Data downloaded | Data downloaded. Monitor removed | REMOVED | REMOVED | REMOVED | REMOVED
FM82 | [6 empty] | SS66944703.1 |  |  | 2024-07-18 | Estate.agreed.loved | Side road of pentrechwtyth Road, SA1 7FR | SS66944704 | X | 450 | 450 | C | 1700 | SS66944704 | 450 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Telemetry data downloaded | Telemetry data downloaded | Telemetry data downloaded | Data downloaded. Monitor removed | REMOVED | REMOVED
FM83 | [6 empty] | SS64949718.1 |  |  | 2024-07-16 | Deck.nail.merit | In layby off Gorse Mission, Carmarthen Rd, Cwmbwrla, Swansea SA5 8LP | SS64949705 | A | 900 | 900 | C | 3520 | SS64949705 | 900 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Telemetry data downloaded | Surcharged. Data downloaded | Steady flow. Sensor cleaned from ragging. Data downloaded | Surcharged. Data downloaded | Steady flow. Sensor cleaned from ragging and grease. Data downloaded | Slow flow. Sensor cleaned from ragging and grease. Data downloaded
FM84 | [6 empty] | ss64949723.2 |  |  | 2024-07-16 | Banana.walks.leans | In layby off Gorse Mission, Carmarthen Rd, Cwmbwrla, Swansea SA5 8LP | SS64949704 | A | 375 | 375 | C | 3790 | SS64949704 | 450 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Telemetry data downloaded | Telemetry data downloaded | Surcharged. Data downloaded | Steady flow. Sensor cleaned from ragging and grease. Data downloaded | Fast flow. Sensor clear but wiped anyway. Data downloaded | Surcharged, so unable to enter. Data downloaded
FM85 | [6 empty] | SS64949501.1 - SHOULD BE DUAL SEWER |  |  | 2024-07-24 | After.avoid.truth | Gors avenue, outside garage, SA1 6RQ | SS65940503 | A | 375 | 375 | C | 2190 | SS65940503 | 525 - check pre-install card | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Steady flow. Sensor cleaned from ragging. Data downloaded | Telemetry data downloaded | Telemetry data downloaded | Steady flow. Sensor cleaned from ragging. Data downloaded | Fast flow. Sensor cleaned from ragging and grease. Data downloaded | Steady flow. Sensor cleaned from ragging and grease. Data downloaded
FM86 | [6 empty] | SS64949501.1 - SHOULD BE DUAL SEWER |  |  | 2024-07-24 | After.avoid.truth | Gors avenue, outside garage, SA1 6RQ | SS65940503 | B | 525 | 525 | C | 1400 | SS65940503 | 375 - check pre-install card | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Steady flow. Sensor cleaned from ragging and re calibrated due to minus readings. | Fast flow. Sensor clear but wiped anyway. Data downloaded | Telemetry data downloaded | Steady flow. Sensor cleaned from ragging. Data downloaded | Fast flow. Sensor cleaned from ragging and grease. Data downloaded | Steady flow. Sensor cleaned from ragging and grease. Data downloaded
FM87 | [6 empty] | SS65941602.1 |  | YES | 2024-07-31 | Treat.reds.fetch | Carmarthen Rd Filter lane to Gors Avenue, SA5 8NJ | SS65940608 | A | 300 | 300 | C | 2280 | SS65940608 | 375 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Slow flow. Sensor cleaned from ragging. Data downloaded | Steady flow. Sensor cleaned from ragging. Data downloaded | Steady flow. Sensor cleaned from ragging and grease. Data downloaded | Steady flow. Sensor cleaned from ragging. Data downloaded | Steady flow. Sensor cleaned from ragging and grease. Data downloaded | Steady flow. Sensor cleaned from ragging and grease. Data downloaded
FM88 | [6 empty] | SS65947207.1 |  |  | 2024-07-19 | Garden.flood.paths | Cwm Road, Before cso SA1 2AY | SS65947210 | X | 900 | 900 | C | 3940 | SS65947210 | 910 x 1200mm brick egg pipe | Outgoing | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Fast flow. Sensor cleaned from ragging and grease. Data downloaded | Fast flow. Sensor clear but wiped anyway. Data downloaded | Fast flow. Sensor clear but wiped anyway. Data downloaded | Fast flow. Sensor clear but wiped anyway. Data downloaded | Fast flow. Sensor clear but wiped anyway. Data downloaded | Fast flow. Sensor cleaned from ragging and grease. Data downloaded
FM89 | [9 empty] | Scrapped | [16 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Telemetry data downloaded | SCRAPPED | SCRAPPED | SCRAPPED | SCRAPPED | SCRAPPED
FM90 | [6 empty] | SS64949201.1 |  |  | 2024-07-19 | Plays.scary.wanted | Near 60-42 Granogwen Rd, Mayhill, Swansea SA1 6UW | SS64949202 | A | 225 | 225 | C | 2100 | SS64949202 | 225 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Trickle flow. Sensor cleaned from ragging. Data downloaded | Slow flow. Sensor cleaned from ragging. Data downloaded | Trickle flow. Sensor cleaned from ragging. Data downloaded | Slow flow. Sensor cleaned from ragging. Data downloaded | Steady flow. Sensor cleaned from ragging and grease. Data downloaded | Trickle flow. Sensor cleaned from ragging and grease. Data downloaded
FM91 | [6 empty] | SS64948101.1 |  |  | 2024-07-19 | Person.region.charge | Outside of house number 340, in the middle of the road next to a central divider, SA1 6PB | SS64949104 | A | 225 | 225 | C | 2010 | SS64949104 | 225 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Telemetry data downloaded | Telemetry data downloaded | Telemetry data downloaded | Steady flow. Sensor cleaned from ragging. Data downloaded | Fast flow. Sensor cleaned from ragging and grease. Data downloaded | Steady flow. Sensor cleaned from ragging and grease. Data downloaded
FM92 | JF |  |  | Removed and relocated to FM161 12/09 |  |  | STORM NETWORK NOT IN ICM |  |  | 2024-07-25 | Spoken.shelf.back | Outside 28 granogwen road | SS64949103 SS64949108 (storm line) | A | 450 | 450 | C | 1600 | SS64949103 | 450 | Incoming | No |  |  |  | Found to be installed in storm line, moved 12/09 to FM161 | #REF! | #REF! | #REF! | #REF! | #REF! | Steady flow. Sensor cleaned from ragging and grease. Data downloaded. Sensor relocated to C pipe | Removed, relocated to FM161 | Removed, relocated to FM161 | Removed, relocated to FM161 | Removed, relocated to FM161 | Removed, relocated to FM161
FM93 | [6 empty] | SS64949101.1 |  |  | 2024-07-19 | Retire.blaze.grid | Infront of a bus stop, outside the Premier shop Near Mayhill Post Office, Mayhill, Swansea SA1 6PA | SS65940202 | A | 225 | 225 | C | 1570 | SS65940202 | 225 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Dry pipe. Sensor clear but wiped anyway. Data downloaded | Telemetry data downloaded | Dry pipe. Sensor cleaned from debris. Data downloaded | Dry pipe. Sensor clear but wiped anyway. Data downloaded | Dry pipe. Sensor clear but wiped anyway. Data downloaded | Dry pipe. Sensor clear but wiped anyway. Data downloaded
FM94 | [6 empty] | SS66932303.1 |  |  | 2024-07-17 | Pounds.nail.blur | In car park opposite Kelly's barbers, SA1 8AT | SS66932202 | A | 525 | 525 | C | 5650 | SS66932202 | 686 x 487 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Telemetry data downloaded | Telemetry data downloaded | Steady flow. Sensor cleaned from ragging and grease. Data downloaded | Steady flow. Sensor cleaned from ragging. Data downloaded | Steady flow. Sensor cleaned from ragging and grease. Data downloaded | Steady flow. Sensor cleaned from ragging and grease. Data downloaded
FM95 | [6 empty] | SS66943004.1 |  |  | 2024-07-18 | Patio.yard.cares | Walk way next to Pentreguinea rd, SA1 8DR | SS66932905 | A | 1200 | 1200 | C | 3450 | SS66932905 | 1200 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Telemetry data downloaded | Fast flow. Sensor clear but wiped anyway. Data downloaded | Fast flow. Sensor clear but wiped anyway. Data downloaded | Fast flow. Sensor clear but wiped anyway. Data downloaded | Fast flow. Sensor clear but wiped anyway. Data downloaded | Fast flow. Sensor clear but wiped anyway. Data downloaded
FM96 | JF |  |  | Removal Requested 19/09 |  |  | SS65934105.1 |  |  | 2024-08-02 | Lush.jeeps.crisis | Outside 61 The Kingsway, SA1 5HN | SS65933105 | A | 300 | 300 | C | 3800 | SS65933105 | 300 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Data downloaded. Monitor removed | REMOVED | REMOVED | REMOVED | REMOVED | REMOVED
FM97 | [6 empty] | SS65929905.1 |  |  | 2024-07-16 | Trial.onions.guess | On path by Morgans, hotel and restaurant sign near traffic lights, SA1 1RR | SS65929806 | A | 600 | 600 | C | 6080 | SS65929806 | 600 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Telemetry data downloaded | Telemetry data downloaded | Steady flow. Sensor cleaned from ragging and grease. Data downloaded | Steady flow. Sensor cleaned from ragging and grease. Data downloaded | Steady flow. Sensor clear but wiped anyway. Data downloaded | Steady flow. Sensor cleaned from ragging and grease. Data downloaded
FM98 | [6 empty] | SS65929905.1 |  | YES | 2024-07-31 | Commented.closes.beats | In left lane of Princess way, SA1 3NE | SS65927704 | X | 1050 | 1050 | C | 5430 | SS65927705 | 457 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Slow flow. Sensor cleaned from ragging and grease. Data downloaded | Steady flow. Sensor clear but wiped anyway. Data downloaded | Slow flow. Sensor cleaned from ragging. Data downloaded | Slow flow. Sensor cleaned from ragging. Data downloaded | Steady flow. Sensor cleaned from ragging and grease. Data downloaded | Steady flow. Sensor cleaned from ragging and grease. Data downloaded
FM99 | [6 empty] | SS65924701.1 |  |  | 2024-07-31 | Pitch.yards.shift | Wellington Street Opposite mspc, Wellington Street Opposite mspc | SS65924703 | A | 1050 | 1050 | C | 4010 | SS65924703 | 900 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Very slow flow - almost standing water. Sensor cleaned from ragging and grease. Data downloaded | Telemetry data downloaded | Telemetry data downloaded | Slow flow. Sensor cleaned from ragging. Data downloaded | Slow flow. Sensor clear but wiped anyway. Data downloaded | Slow flow. Sensor cleaned from ragging and grease. Data downloaded
FM100 | [6 empty] | SS64929504.1 |  | YES | 2024-08-06 | Giving.cake.softly | Argyle St outside no 11 in parking bay, SA1 3TA | SS64929401 | A | 2134 | 2134 | C | 4700 | SS64929401 | 900 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Unable to enter. Parked car on manhole. No response to notes previously left on car | Telemetry data downloaded | Steady flow. Sensor cleaned from ragging and grease. Sensor calibrated to match manual measurements. Data downloaded | Unable to access due to parked car | Unable to make entry due to parked car. Data downloaded
FM101 | [9 empty] | Scrapped | [16 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Telemetry data downloaded | SCRAPPED | SCRAPPED | SCRAPPED | SCRAPPED | SCRAPPED
FM102 | [9 empty] | Scrapped | [16 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Telemetry data downloaded | SCRAPPED | SCRAPPED | SCRAPPED | SCRAPPED | SCRAPPED
FM103 | JF |  |  | Removal Requested 19/09 |  |  | SS64923606.1 |  | YES | 2024-08-01 | Sleepy.tigers.than | King Edwards Rd, junction of St Helens crescent, SA1 4NG | SS64923508 | A | 1676 | 1676 | C | 2200 | SS64923508 | 1676 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Very slow flow - almost standing water. Sensor cleaned from ragging and grease. Data downloaded | Data downloaded. Monitor removed | REMOVED | REMOVED | REMOVED | REMOVED
FM104 | JF |  |  | Removal Requested 19/09 |  |  | SS62929702.1 |  |  | 2024-07-16 | Lasted.wide.soup | Singleton Park near gate, SA2 9BY | SS62929702 | B | 600 | 600 | C | 2300 | SS62929702 | 450 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Fast flow, sensor cleaned from heavy ragging. Data downloaded | Data downloaded. Monitor removed | REMOVED | REMOVED | REMOVED | REMOVED
FM105 | JF |  |  | Removal Requested 19/09 |  |  | SS62929703.1 |  |  | 2024-07-16 | Lasted.wide.soup | Singleton Park near gate, SA2 9BY | SS62929702 | A | 450 | 450 | C | 2300 | SS62929702 | 600 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Fast flow, sensor cleaned from heavy ragging. Data downloaded | Data downloaded. Monitor removed | REMOVED | REMOVED | REMOVED | REMOVED
FM106 | [6 empty] | SS63923304.1 |  |  | 2024-07-18 | Pies.posts.bound | Singleton Park by entrance of brynmill coffee house, SA2 0BB | SS63923306 | A | 450 | 450 | C | 1880 | SS63923306 | 375 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Steady flow. Sensor cleaned from ragging and grease. Sensor recalibrated to match manual measurements. Data downloaded | Steady flow. Sensor cleaned from ragging and grease. Data downloaded | Data downloaded. Monitor removed | REMOVED | REMOVED | REMOVED
FM107 | [6 empty] | SS63923103.2 |  |  | 2024-07-16 | Record.notice.burns | Singleton Park opposite side to fm104, SA2 8PP | SS63923104 | A | 975 | 975 | C | 1980 | SS63923104 | 450 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Steady flow, sensor cleaned - data downloaded | Telemetry data downloaded | Telemetry data downloaded | Steady flow. Sensor cleaned from ragging and grease. Data downloaded | Steady flow. Sensor cleaned from ragging and grease. Data downloaded | Steady flow. Sensor cleaned from ragging and grease. Data downloaded
FM108 | [6 empty] | SS63925002.1 |  |  | 2024-08-06 | Pints.flies.nods | Near Brynmill, Swansea, SA2 0AU | SS63914905 | B | 1650 | 1650 | C | 2720 | SS63925001 | 1676 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Slow flow. Sensor cleaned from ragging and grease. Sensor recalibrated to match manual measurements. Data downloaded | Telemetry data downloaded | Telemetry data downloaded | Steady flow. Sensor cleaned from ragging. Data downloaded | Slow flow. Sensor cleaned from ragging and grease. Data downloaded | Slow flow. Sensor clear but wiped anyway. Data downloaded
FM109 | [9 empty] | Scrapped | [16 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Telemetry data downloaded | SCRAPPED | SCRAPPED | SCRAPPED | SCRAPPED | SCRAPPED
FM110 | [6 empty] | 61929903.2 |  |  | 2024-07-16 | Fault.festivity.water | Ty Derw Car Park, SA2 8BP | SS61929916 | X | 300 | 300 | C | 2230 | SS61929908 | 450 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Fast flow. Sensor cleaned from ragging and grease. Data downloaded | Telemetry data downloaded | Fast flow. Sensor clear but wiped anyway. Data downloaded | Fast flow. Sensor cleaned from ragging and grease. Data downloaded | Steady flow. Sensor cleaned from ragging and grease. Data downloaded | Very fast flow- Spraying up against sensor. Sensor clear but wiped anyway. Data downloaded
FM111 | [6 empty] | GYA-1.1 |  |  | 2024-07-24 | Walks.first.delay | Roger blackmore autos Towards back of carpark, SA2 9JH | SS61939006 | A | 400 | 400 | C | 2820 | SS61939006 | 400 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Telemetry data downloaded | Telemetry data downloaded | Fast flow. Sensor cleaned from ragging and grease. Data downloaded | Steady flow. Sensor clear but wiped anyway. Data downloaded | Fast flow. Sensor cleaned from ragging and grease. Data downloaded | Fast flow. Sensor clear but wiped anyway. Data downloaded
FM112 | JF |  |  | Removed and relocated to FM162 16/09 |  |  | SS61929902.1 |  | YES | 2024-07-16 | River.dairy.saints | Ty Derw Road to further parking, SA2 8BP | SS61929911 | X | 300 | 300 | C | 2870 | SS619299902 | 300 | Incoming |  |  |  |  | Relocated on 16/09 to FM162 | #REF! | #REF! | #REF! | #REF! | #REF! | Fast flow. Data downloaded. Monitor removed and recalibrated for relocation. Sensor cleaned from grease. Monitor relocated | Removed, relocated to FM162 | Removed, relocated to FM162 | Removed, relocated to FM162 | Removed, relocated to FM162 | REMOVED
FM113 | [9 empty] | Scrapped | [16 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Telemetry data downloaded | SCRAPPED | SCRAPPED | SCRAPPED | SCRAPPED | SCRAPPED
FM114 | [6 empty] | SS61909802.1 |  |  | 2024-07-19 | Goat.took.skips | Near Blackpill, Sketty, Swansea SA2 8EJ | SS61909802 | B | 550 | 550 | C | 2170 | SS61909802 | 550 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Steady flow. Sensor cleaned from ragging and grease. Data downloaded | Steady flow. Sensor cleaned from ragging and grease. Sensor calibrated to match manual measurements. Data downloaded | Fast flow. Sensor cleaned from ragging and grease. Data downloaded | Steady flow. Sensor cleaned from ragging and grease. Data downloaded | Steady flow. Sensor cleaned from ragging and grease. Data downloaded | Fast flow. Sensor cleaned from ragging and grease. Data downloaded
FM115 | [6 empty] | SS61907801 |  |  | 2024-07-19 | Plants.swing.caked | Derwen fair road, outside Brook villa, SA3 5AT | SS61908801 | A | 450 | 450 | C | 1900 | SS61908801 | 450 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Steady flow. Sensor cleaned from ragging and grease. Sensor recalibrated to match manual measurements. Data downloaded | Steady flow. Sensor cleaned from ragging and grease. Sensor calibrated to match manual measurements. Data downloaded | Steady flow. Sensor cleaned from ragging and grease. Data downloaded | Steady flow. Sensor cleaned from ragging and grease. Data downloaded | Steady flow. Sensor cleaned from ragging and grease. Data downloaded | Steady flow. Sensor cleaned from ragging and grease. Data downloaded
FM116 | [6 empty] | SS61917102.1 |  |  | 2024-07-25 | Goes.lanes.flat | Derwen road before glynderwen cresent | SS61918005 | A | 375 | 375 | C | 4380 | SS61918005 | 600 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | Sensor blown out on arrival - SITE REMOVED. | Turbulent flow had pushed sensor and ring out of pipe. Monitor removed. Awaiting further instruction for potential relocation. | Site visit required - unit does not dial in through the internet | Removed, relocated to FM163 | Removed, relocated to FM163 | Removed, relocated to FM163 | Removed, relocated to FM163
FM117 | [6 empty] | SS61906301.1 |  |  | 2024-08-02 | Shady.onion.names | 3-9 Mayals Rd, Mayals, West Cross, SA3 5BT | SS61907301 | A | 300 | 300 | C | 2730 | SS61907301 | 300/375 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | Sensor blown out on arrival - SITE REMOVED. | Fast turbulent flow. Sensor had become dislodged from pipe. Sensor cleaned re fitted in pipe and thoroughly secured | Fast flow. Senseor cleaned from ragging and grease. Data downloaded | Steady flow. Heavy ragging. Sensor cleaned and monitor removed, to be relocated. Awaiting further instruction | Steady flow. Sensor cleaned from ragging and grease. Data downloaded | Steady flow. Sensor cleaned from ragging and grease. Data downloaded | Steady flow. Sensor cleaned from ragging and grease. Data downloaded
FM118 | [6 empty] | SS61908302.1 |  |  | 2024-07-22 | Vines.lied.table | Grass off mumbles Road, opposite 154, SA3 5AW | SS61907201 | A | 1700 | 1700 | C | 2890 | SS61907201 | 2286 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Steady flow. Sensor cleaned from heavy ragging. Data downloaded | Telemetry data downloaded | Telemetry data downloaded | Steady flow. Sensor cleaned from ragging and grease. Data downloaded | Slow flow. Sensor cleaned from ragging and grease. Data downloaded | Slow flow. Sensor cleaned from ragging and grease. Data downloaded
FM119 | JF |  |  | Removal Requested 19/09 |  |  | SS60899901.1 |  | YES | 2024-07-23 | Tour.puts.cities | Fairwood Road, on pavement outside Holy Cross church | SS60899904 | X | 225 | 225 | C | 1960 | SS60899904 | 225 | Outgoing | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Telemetry data downloaded | Data downloaded. Monitor removed | REMOVED | REMOVED | REMOVED | REMOVED
FM120 | JF |  |  | Removal Requested 19/09 |  |  | SS61891801.1 |  |  | 2024-08-02 | Until.acting.dated | Outside no 43 fairwood rd, SA3 5LA | SS61891801 | A | 225 | 225 | C | 2700 | SS61891801 | 300 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Steady flow. Sensor cleaned from ragging and grease. Data downloaded | Data downloaded. Monitor removed | REMOVED | REMOVED | REMOVED | REMOVED
FM121 | [6 empty] | SS61894002.1 |  |  | 2024-08-01 | Utensil.campus.scrub | Mumbles rd Junction of bethany lane, SA3 5TB | SS61894002 | A | 375 | 375 | C | 1840 | SS61894002 | 375/450 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Telemetry data downloaded | Telemetry data downloaded | Telemetry data downloaded | Steady flow. Sensor cleaned from ragging. Data downloaded | Steady flow. Sensor clear but wiped anyway. Data downloaded | Steady flow. Sensor cleaned from ragging and grease. Data downloaded
FM122 | JF |  |  | Removal Requested 19/09 |  |  | SS61881702.1 |  | YES | 2024-08-01 | Upward.period.minority | Junction of Castle Rd and Glen rd, SA3 5TF | SS61881702 | X | 300 | 300 | C | 2040 | SS61881702 | 300 | Outgoing | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Steady flow. Sensor and ring had dislodged from pipe. Sensor cleaned and refitted and thoroughly secured | Telemetry data downloaded | REMOVED | REMOVED | REMOVED | REMOVED
FM123 | JF |  |  | Removal Requested 19/09 |  |  | SS61881903.1 |  |  | 2024-07-25 | Fees.proven.pronouns | Westcross avenue, on road outside Norton villa clinic | SS61881704 | X | 225 | 225 | C | 1830 | SS61881704 | 225 | Outgoing | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Steady flow. Sensor cleaned from ragging. Data downloaded | Data downloaded. Monitor removed | REMOVED | REMOVED | REMOVED | REMOVED
FM124 | [6 empty] | SS61883701.1 |  |  | 2024-08-01 | Seagulls.crate.recorder | Norton Rd Outside 4A where rd narrows, SA3 5TQ | SS61884712 | A | 300 | 300 | C | 1760 | SS61884712 | 300 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Telemetry data downloaded | Moniotr swapped - sensor refitted. | Steady flow. Sensor cleaned from ragging. Data downloaded | Fast flow. Sensor cleaned from grease. Data downloaded | Fast flow. Data downloaded. Monitor swapped due to format error. | Steady flow. Sensor clear but wiped anyway. Data downloaded
FM125 | [6 empty] | SS60885001.1 |  |  | 2024-08-09 | Agency.rejoins.layered | By wall off Southward Lane Nottage road junction, SA3 4SU | SS60885001 | X | 225 | 225 | C | 2450 | SS60885001 | 225 | Outgoing | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Steady flow. Sensor cleaned from heavy ragging. Data downloaded | Telemetry data downloaded | Telemetry data downloaded | Steady flow. Sensor cleaned from ragging and grease. Data downloaded | Unable to access due to parked car - telemetry data downloaded | Unable to access due to parked car
FM126 | JF |  |  | Removed and relocated to FM163 18/09 |  |  | SS60885002.1 |  |  | 2024-07-25 | Regulates.sadly.discouraged | New well lane, junction off of Newton road | SS60886101 | B | 300 | 300 | C | 2650 | SS60886101 | 300 | Incoming |  |  |  |  | Relocated on 18/09 to FM163 | #REF! | #REF! | #REF! | #REF! | #REF! | Data downloaded. Monitor removed. Sensor cleaned from ragging. Monitor relocated | Removed, relocated to FM163 | Removed, relocated to FM163 | Removed, relocated to FM163 | Removed, relocated to FM163 | Removed, relocated to FM163
FM127 | JF |  |  | Removed and relocated to FM164 05/09 |  |  | SS60886102.1 |  |  | 2024-07-26 | Shallower.juicy.respected | Newton Rd Outside no 114 | SS60886002 | A | 300 | 300 | C | 2100 | SS60886011 | 300 | Incoming |  |  |  |  | Relocated on 05/09 to FM164 | #REF! | #REF! | #REF! | #REF! | #REF! | Steady flow. Sensor cleaned from ragging and grease. Data downloaded | Removed, relocated to FM164 | Removed, relocated to FM164 | Removed, relocated to FM164 | Removed, relocated to FM164 | Removed, relocated to FM164
FM128 | [6 empty] | SS60887001.1 |  |  | 2024-07-30 | Reclined.footballers.rejoins | Near 3436 Newton Rd, Langland, Newton, Swansea SA3 4SW | SS60887002 | A | 225 | 225 | C | 2900 | SS60887002 | 225 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Steady flow. Sensor cleaned from ragging and grease. Data downloaded | Fast flow. Sensor clear but wiped anyway. Data downloaded | Steady flow. Sensor cleaned from ragging and grease. Sensor calibrated to match manual measurements. Data downloaded | Steady flow. Sensor cleaned from grease. Data downloaded | Steady flow. Sensor cleaned from grease. Data downloaded | Fast flow. Sensor cleaned from ragging and grease. Data downloaded
FM129 | [6 empty] | SS60889002.1 |  | YES | 2024-07-23 | Conqueror.closes.stocks | Undersell hub Next to track on grass | SS60889001 | X | 375 | 375 | C | 1500 | SS60889001 | 375 | Outgoing | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Slow flow. Sensor cleaned from ragging and grease. Data downloaded | Steady flow. Sensor cleaned from ragging. Data downloaded | Slow flow. Sensor cleaned from ragging and grease. Data downloaded | Trickle flow. Sensor cleaned from ragging and grease. Data downloaded | Slow flow. Sensor cleaned from ragging and grease. Data downloaded | Slow flow. Sensor cleaned from ragging and grease. Data downloaded
FM130 | [6 empty] | SS60889001.1 |  |  | 2024-07-26 | Scooter.nightfall.voters | Newton Rd next to track to underhill hub | SS60889102 | B | 300 | 300 | C | 2900 | SS60889102 | 375 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Trickle flow. Sensor cleaned from grease. Data downloaded | Slow flow. Sensor cleaned from ragging. Data downloaded | Dry pipe. Sensor clear but wiped anyway. Data downloaded | Steady flow. Sensor cleaned from ragging and grease. Data downloaded | Dry pipe. Sensor clear but wiped anyway. Data downloaded | Dry pipe. Sensor clear but wiped anyway. Data downloaded
FM131 | [6 empty] | SS61885203.1 |  |  | 2024-07-26 | Grad.truth.shot | Mumbles Rd, opposite bus stop | SS61885203 | A | 450 | 450 | C | 4930 | SS61885203 | 450 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Slow flow. Sensor cleaned from ragging and silt. Sensor offsett to avoid further silt. Data downloaded | Slow flow. Sensor cleaned from ragging. Data downloaded | Slow flow. Sensor cleaned from silt. Sensor repositioned to 5 o'clock offset to avoid further issues with silt. Data downloaded | Slow flow. Sensor cleaned from grease. Data downloaded | Slow flow. Sensor clear but wiped anyway. Data downloaded | Slow flow. Sensor clear but wiped anyway. Data downloaded
FM132 | [6 empty] | SS61885201.1 |  | YES | 2024-07-25 | Trains.truffles.normal | Newton Road, outside coakleys fishmonger | SS61885271 | A | 375 | 375 | C | 3200 | SS61885271 | 375 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Telemetry data downloaded | Telemetry data downloaded | Telemetry data downloaded | Fast flow. Sensor cleaned from grease. Data downloaded | Fast flow. Sensor cleaned from ragging and grease. Data downloaded | Fast flow. Sensor clear but wiped anyway. Data downloaded
FM133 | [6 empty] | SS61886101.3 |  | YES | 2024-07-26 | Throwaway.cupboards.liberated | Mumbles road, junction of dunns lane | SS61886101 | A | 600 | 600 | C | 2360 | SS61886101 | 600 | Outgoing | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Telemetry data downloaded | Telemetry data downloaded | Telemetry data downloaded | Steady flow. Sensor cleaned from grease. Data downloaded | Fast flow. Sensor cleaned from ragging and grease. Data downloaded | Steady flow. Sensor cleaned from ragging and grease. Data downloaded
FM134 | [6 empty] | SS61885103.1 |  |  | 2024-07-26 | Throwaway.cupboards.liberated | Mumbles road, junction of dunns lane | SS61886102 | X | 600 | 600 | C | 2360 | SS61886101 | 600 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Site visit required - unit does not dial in through the internet | Site visit required - unit does not dial in through the internet | Steady flow. Sensor cleaned from ragging and grease. Data downloaded | Steady flow. Sensor cleaned from ragging. Data downloaded | Fast flow. Sensor cleaned from ragging and grease. Data downloaded | Steady flow. Sensor cleaned from ragging and grease. Data downloaded
FM135 | [6 empty] | SS61879805.2 |  | YES | 2024-07-26 | Balloons.approvals.stole | Mumbles road outside the ponderosa | SS61879801 | Y | 450 | 450 | C | 2810 | SS61879801 | 450 | Outgoing | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Dry pipe. Sensor clear but wiped anyway. Data downloaded | Telemetry data downloaded | Dry pipe. Sensor clear but wiped anyway. Data downloaded | Dry pipe. Sensor clear but wiped anyway. Data downloaded | Dry pipe. Sensor clear but wiped anyway. Data downloaded | Dry pipe. Sensor clear but wiped anyway. Data downloaded
FM136 | JF |  |  | Removal Requested 19/09 |  |  | SS61878902.1 |  |  | 2024-07-26 | Trucks.caressed.fines | Outside mint of mumbles, mumbles road | SS61878803 | A | 450 | 450 | C | 2640 | SS61878803 | 450 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Data downloaded. Monitor removed | REMOVED | REMOVED | REMOVED | REMOVED | REMOVED
FM137 | JF |  |  | Removal Requested 19/09 |  |  | SS61879801.1 |  |  | 2024-07-26 | Balloons.approvals.stole | Mumbles road outside the ponderosa | SS61879801 | B | 450 | 450 | C | 2810 | SS61879801 | 600 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Data downloaded. Monitor removed | REMOVED | REMOVED | REMOVED | REMOVED | REMOVED
FM138 | [6 empty] | SS62872702.1 |  | YES | 2024-08-01 | Meanwhile.defensive.blushed | Mumbles Rd Outside no 2 Chandler's Reach | SS62672750 | C | 450 | 450 | C | 3700 | SS62872750 | 450 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Telemetry data downloaded | Telemetry data downloaded | Telemetry data downloaded | Slow flow. Sensor cleaned from ragging. Data downloaded | Slow flow. Unable to make entry due to close parked car. Data downloaded | Slow flow. Sensor clear but wiped anyway. Data downloaded
FM139 | [6 empty] | SS62874201.1 |  |  | 2024-07-19 | Unzipped.cowering.jokers | Plunch LN, mumbles swansea SA3 4JE | SS62875105 | A | 225 | 225 | C | 2300 | SS62875105 | 225/300 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Steady flow. Sensor cleaned from ragging and grease. Sensor recalibrated to match manual measurements. Data downloaded | Steady flow. Sensor clear but wiped anyway. Data downloaded | Steady flow. Sensor clear but wiped anyway. Data downloaded |  | Steady flow. Sensor cleaned from ragging and grease. Data downloaded | Steady flow. Sensor cleaned from ragging and grease. Data downloaded
FM140 | JF |  |  | Removal Requested 19/09 |  |  | SS71935201.1 |  |  | 2024-07-19 | Ticked.announced.because | On grass land behind pumpstation, SA10 6JL | SS71936202 | X | 600 | 600 | C | 3200 | SS71936202 | 600 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Steady flow. Sensor cleaned from ragging and grease. Data downloaded | Data downloaded. Monitor removed | REMOVED | REMOVED | REMOVED | REMOVED
FM141 | JF |  |  | Removal Requested 19/09 |  |  | SS64959903.1 |  |  | 2024-07-23 | Lies.glee.caves | Outside no 3 trigfa penlan fach | SS64959901 | B | 300 | 300 | C | 1950 | SS64959901 | 375 | Incoming Pipe | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Data downloaded. Monitor removed | REMOVED | REMOVED | REMOVED | REMOVED | REMOVED
FM142 | [6 empty] | SS64958802.1 |  |  | 2024-07-23 | Lies.glee.caves | Outside no 3 trigfa penlan fach | SS64959901 | A | 375 | 375 | C | 1950 | SS64959901 | 225 | Incoming PIpe | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Data downloaded. Monitor removed | REMOVED | REMOVED | REMOVED | REMOVED | REMOVED
FM143 | JF |  |  | Removal Requested 19/09 |  |  | SS65950801.1 |  |  | 2024-07-26 | Risen.rotate.danger | Field off penlan fach | SS65951801 | A | 225 | 225 | C | 1800 | SS65951801 | 225 | Incoming Foul Pipe | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | REMOVED | REMOVED | REMOVED | REMOVED | REMOVED | REMOVED
FM144 | [6 empty] | SS65952802.1 |  | YES | 2024-07-26 | Shells.funds.wooden | Amongst bushes off patn off Bryn street | SS65952850 | A | 225 | 225 | C | 2200 | SS65952850 | 225 | Incoming Foul Pipe | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Fast flow, sensor cleaned from heavy ragging. Data downloaded | Telemetry data downloaded | Data downloaded. Monitor removed | REMOVED | REMOVED | REMOVED
FM145 | JF |  |  | Removal Requested 19/09 |  |  | STORM NETWORK DOES NOT EXIST IN ICM |  |  | 2024-07-26 | Risen.rotate.danger | Field off penlan fach | SS65951801 | B | 525 | 525 | C | 1800 | SS65951801 | 525 | Incoming Storm Pipe | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | REMOVED | REMOVED | REMOVED | REMOVED | REMOVED | REMOVED
FM146 | [6 empty] | SS65952803.1 |  |  | 2024-07-26 | Think.aside.actor | End of Bryn street | SS65953808 | A | 686 | 686 | C | 2670 | SS65953808 | 686 | Incoming pipe | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Car parked on MH | Telemetry data downloaded | Data downloaded. Monitor removed | Data downloaded. Monitor removed | REMOVED | REMOVED
FM147 | [6 empty] | SS63921401.1 |  |  | 2024-07-18 | Media.index.ideal | Singleton Park in the field between trees, SA2 0BB | SS63922401 | A | 600 | 600 | C | 3020 | SS63922401 | 500 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Fast flow. Sensor cleaned from ragging and grease. Data downloaded | Site visit required - unit does not dial in through the internet | Telemetry data downloaded | Telemetry data downloaded | REMOVED | REMOVED
FM148 | JF |  |  | Removal Requested 19/09 |  |  | STORM NETWORK DOES NOT EXIST IN ICM |  |  | 2024-07-25 | Finely.preoccupied.cape | Corner of penlan terrace | SS65960602 | X | 525 | 525 | C | 2800 | SS65960602 | 305 | Outgoing (Storm) | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Data downloaded. Monitor removed | REMOVED | REMOVED | REMOVED | REMOVED | REMOVED
FM149 | [6 empty] | SS65924801.1 |  | YES | 2024-07-25 | Think.aside.actor | Pavement by shopping mall next to bins | SS65923802 | X | 1100 | 1100 | C | 4060 | SS65923802 | 1050 | Outgoing | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Telemetry data downloaded | Telemetry data downloaded | Telemetry data downloaded | Steady flow. Sensor cleaned from ragging and grease. Data downloaded | Steady flow. Sensor cleaned from ragging and grease. Data downloaded | Steady flow. Sensor cleaned from ragging and grease. Data downloaded
FM150 | JF |  |  | Removal Requested 19/09 |  |  | SS65934103.1 |  |  | 2024-08-02 | Lush.jeeps.crisis | Outside 61 The Kingsway, SA1 5HN | SS65933105 | X | 300 | 300 | C | 3800 | SS65933105 | 575 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Data downloaded. Monitor removed | REMOVED | REMOVED | REMOVED | REMOVED | REMOVED
FM151 | [6 empty] | SS64949724.1 |  |  | 2024-08-12 | Pilots.good.tone | On grass verge of Three Sisters Island, across the road from boots optiticians, SA5 8LW | SS64948716 | A | 600 | 600 | C | 3200 | SS64948716 | 600 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Telemetry data downloaded | Telemetry data downloaded | Telemetry data downloaded | Steady flow. Sensor cleaned from grease. Data downloaded | Fast flow. Sensor clear but wiped anyway. Data downloaded | Fast flow. Sensor clear but wiped anyway. Data downloaded
FM152 | [6 empty] | SS64948715.1 |  |  | 2024-08-12 | Bound.diary.vest | On verge of Three Sisters Island, next to boots by electric kiosk, SA5 8LW | SS64948714 | A | 900 | 900 | C | 3600 | SS64948714 | 900 | Incoming | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Telemetry data downloaded | Telemetry data downloaded | Telemetry data downloaded | Fast flow. Sensor clear but wiped anyway. Data downloaded | Fast flow. Sensor clear but wiped anyway. Data downloaded | Fast flow. Sensor clear but wiped anyway. Data downloaded
FM153 | [6 empty] | SS64946601.1 | [19 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Steady flow. Sensor cleaned from ragging. Data downloaded | Telemetry data downloaded | Telemetry data downloaded | Steady flow. Sensor cleaned from ragging and grease. Data downloaded | Steady flow. Sensor clear but wiped anyway. Data downloaded | Steady flow. Sensor cleaned from ragging and grease. Data downloaded
FM154 | [6 empty] | SS64946604.1 |  | YES | [17 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Telemetry data downloaded | Telemetry data downloaded | Site visit required - unit does not dial in through the internet | Steady flow. Sensor cleaned from ragging and grease. Data downloaded | Fast flow. Sensor cleaned from ragging and grease. Data downloaded | Fast flow. Sensor cleaned from ragging and grease. Data downloaded
FM155 |  |  |  | Relocation of FM06 |  |  | SS66985301.1 |  | YES | 2024-09-20 | Ledge.gong.acted | Heol y nant outside piccolo bar, SA6 5LG | SN69011308 | A | 525 | 525 | C | 2400 |  |  |  | Yes | Yes | Yes | Yes | [7 empty] | Relocated from FM06 | Relocated from FM06 - Turbulent flow. Sensor claned from ragging and grease. Data downloaded | Relocated from FM06 - Steady flow. Sensor cleaned from grease. Data downloaded | Steady flow. Sensor cleaned from ragging and grease. Data downloaded | Steady flow. Sensor cleaned from ragging and grease. Data downloaded
FM156 |  |  |  | Relocation of FM32 |  |  | SS66997002.1 |  |  | 2024-09-03 | Mug.swung.member | Outside 7 heol dyfan, vicarage road, SA6 6DX | SS66997004 | X | 225 | 225 | C | 1750 |  |  |  | Yes | Yes | Yes | Yes | [7 empty] | Relocated from FM32 - Steady flow. Sensor cleaned from ragging. Data downloaded | Relocated from FM32 - Steady flow. Sensor cleaned from ragging and grease. Data downloaded | Relocated from FM32 - Steady flow. Sensor cleaned from ragging and grease. Data downloaded | Data downloaded. Monitor removed | REMOVED
FM157 |  |  |  | Relocation of FM34 |  |  | SS66985301.1 |  | YES | 2024-09-19 | Fish.trial.hang | 90 Vicarage Rd, Morriston, Swansea SA6 6DP, on junction to Pleasant street | SS66985344 | X | 300 | 300 | C | 3800 |  |  |  | Yes | Yes | Yes | Yes | Install sheet has wrong MH reference (SS66986301), photos etc show that performance sheet is correct | [6 empty] | Relocated from FM34 - Fast flow. Sensor clear but wiped anyway. Data downloaded | Relocated from FM34 - Steady flow. Sensor clear but wiped anyway. Data downloaded | Relocated from FM34 - Steady flow. Sensor clear but wiped anyway. Data downloaded | Steady flow. Sensor clear but wiped anyway. Data downloaded | Steady flow. Sensor clear but wiped anyway. Data downloaded
FM158 |  |  |  | Relocation of FM35 |  |  | SS66989302.1 |  | YES | 2024-09-10 | Echo.shin.loads | Outside 31 pentrepoeth Road in parking bay SA6 6HJ | SH66989301 SS66989301 | X | 300 | 300 | C | 3550 |  |  |  | Yes | Yes | Yes | Yes | [7 empty] | Relocated from FM35 - Fast flow. Sensor clear but wiped anyway. Data downloaded | Relocated from FM35 - Site visit required - unit does not dial in through the internet | Relocated from FM35 - Fast flow. Sensor cleaned from grease. Data downloaded | Fast flow. Sensor cleaned from ragging and grease. Data downloaded
FM159 |  |  |  | Relocation of FM67 |  |  | SS66951905.1 |  | YES | 2024-09-10 | Using.case.blame | Near Plasmarl, SA6 8JT | SS66951970 | X | 800 | 800 | C | 6750 |  |  |  | Yes | Yes | Yes | Yes | [7 empty] | Relocated from FM67 - Steady flow. Sensor clear but wiped anyway. Data downloaded | Relocated from FM67 - Data downloaded. Monitor removed | Relocated from FM67 - REMOVED | REMOVED | REMOVED
FM160 |  |  |  | Relocation of FM70 |  |  | SS65954810.1 |  | YES | 2024-09-10 | Saying.bells.remote | On grass behind bus stop, SA5 9EA | SS65954813 | X | 675 | 675 | C | 3680 |  |  |  | Yes | Yes | Yes | Yes | [7 empty] | Relocated from FM70 - Steady flow. Sensor clear but wiped anyway. Data downloaded | Relocated from FM70 - Telemetry data downloaded | Relocated from FM70 - Site visit required - unit does not dial in through the internet | Site visit required to collect data.
FM161 |  |  |  | Relocation of FM92 |  |  | SS64949103.1 |  |  | 2024-09-12 | System.filed.rugs | Near 85-93 Waun-Wen Rd, Mayhill, Swansea SA1 6UN | SS65940106 | C | 325 | 325 | C | 2740 |  |  |  | Yes | Yes | Yes | Yes | [7 empty] | Relocated from FM92 - Steady flow. Sensor cleaned from ragging and grease. Sensor calibrated to match manual measurements. Data downloaded | Relocated from FM92 - Steady flow. Sensor clear but wiped anyway. Data downloaded | Relocated from FM92 - Steady flow. Sensor cleaned from grease. Data downloaded | Steady flow. Sensor cleaned from grease. Data downloaded
FM162 |  |  |  | Relocation of FM112 |  |  | SS61929803.1 |  |  | 2024-09-16 | Bath.coherent.motor | Hazel Ct, Sketty, Swansea SA2 8BP | SS61929806 | A | 450 | 450 | C | 2450 |  |  |  | Yes | Yes | Yes | Yes | [7 empty] | Relocated from FM112 - Telemetry data downloaded | Relocated from FM112 - Steady flow. Sensor clear but wiped anyway. Data downloaded | Relocated from FM112 - Steady flow. Sensor cleaned from grease. Data downloaded | Data downloaded. Monitor removed | REMOVED
FM163 |  |  |  | Relocation of FM126 |  |  | No spill modelled |  |  | 2024-09-18 | Muted.scarcely.commuted | 121 Newton Rd, Langland, Newton, Swansea SA3 4SW | SS60886003 | B | 300 | 300 | C | 1510 |  |  |  | Yes | Yes | Yes | Yes | [7 empty] | Relocated from FM126 - Site visit required - unit does not dial in through the internet | Relocated from FM126 - Site visit required - unit does not dial in through the internet | Relocated from FM126 - Site visit required - unit does not dial in through the internet | Site visit required to collect data.
FM164 |  |  |  | Relocation of FM127 |  |  | SS60884202.1 |  |  | 2024-09-05 | Fields.instilled.piglet | In the alley next door to new haven house, Spade Rd SA3 4UE | SS60884204 | A | 300 | 300 | C | 2380 |  |  |  | Yes | Yes | Yes | Yes | [7 empty] | Relocated from FM127 - Steady flow. Sensor cleaned from ragging. Data downloaded | Relocated from FM127 - Telemetry data downloaded | Relocated from FM127 - Steady flow. Sensor cleaned from ragging and grease. Data downloaded | Steady flow. Sensor cleaned from ragging. Data downloaded | Steady flow. Sensor cleaned from ragging and grease. Data downloaded
FM165 |  |  |  | Relocation of FM116 | [31 empty] | Fast flow. Sensor cleaned from ragging and grease. Data downloaded | Fast flow. Sensor clear but wiped anyway. Data downloaded
DM01 | [6 empty] | CREATE DUMMY LINK |  |  | 2024-07-25 | Spice.skinny.piper | Fuzeland CSO | CSO |  |  |  |  | 3900 | SS61929910 | - | - | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Telemetry data downloaded | Telemetry data downloaded | Data downloaded. Sensor calibrated to match manual measurements | Access site | Telemetry data downloaded | Telemetry data downloaded
DM02 | [6 empty] | CREATE DUMMY LINK |  |  | 2024-07-24 | Prop.roofs.panels | Elba crescent sps | Wetwell |  |  |  |  | 4170 | 50918 | - | - | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Site visit required - unit does not dial in through the internet | Site visit required - unit does not dial in through the internet | Data downloaded. Monitor removed | REMOVED | REMOVED | REMOVED
DM03 | [6 empty] | CREATE DUMMY LINK |  |  | 2024-07-24 | Analogy.yarn.ships | Baldwins sps | Wetwell |  |  |  |  | 4670 | 50834 | - | - | [5 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Telemetry data downloaded | Site visit required - unit does not dial in through the internet | Data downloaded. Monitor removed | REMOVED | REMOVED | REMOVED
PL01 | [9 empty] | 2024-07-25 | Blotches.drainage.probing | Glais SPS near 19 Y Gwernydd, Glais, Swansea, SA7 9HE | [14 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Access required to download data | Site visit required - unit does not dial in through the internet | Data downloaded. Logger removed | REMOVED | REMOVED | REMOVED
PL02 | JF |  |  | Removal Requested 19/09 | [5 empty] | 2024-07-25 | novels.glue.sing | Birchgrove Road SPS | [14 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Access required to download data | Site visit required - unit does not dial in through the internet | Data downloaded. Logger removed | REMOVED | REMOVED | REMOVED
PL03 | [9 empty] | 2024-07-25 | clubs.stared.heat | CSO Halfway Crymlyn Road PS | [14 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Access required to download data | Site visit required - unit does not dial in through the internet |  | Access site | Access required | Access required
PL04 | [9 empty] | 2024-07-24 | before.look.bossy | Fenrod sps | [14 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Access required to download data | Site visit required - unit does not dial in through the internet | Data downloaded - All okay | Access site | Access required | Access required
PL05 | [9 empty] | 2024-07-24 | Bigger.areas.outburss | Knab rock sps | [14 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Access required to download data | Site visit required - unit does not dial in through the internet |  | Access site | Access required | Access required
PL06 | [9 empty] | 2024-07-24 | nuggets.liberated.neon | Limeslade SPS | [14 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Access required to download data | Site visit required - unit does not dial in through the internet | Data downloaded - All okay | Access site | Access required | Access required
PL07 | [9 empty] | 2024-07-25 | owner.ethic.someone | Fabian Way SPS | [14 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Access required to download data | Site visit required - unit does not dial in through the internet | Data downloaded. Logger removed | REMOVED | REMOVED | REMOVED
PL08 | [9 empty] | 2024-07-24 | prop.roofs.panels | Elba crescent sps | [14 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Access required to download data | Site visit required - unit does not dial in through the internet | No comms, data to be downloaded in workshop. Logger removed | REMOVED | REMOVED | REMOVED
PL09 | [9 empty] | 2024-07-24 | analogy.yarn.ships | Baldwins Crescent SPS | [14 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Access required to download data | Site visit required - unit does not dial in through the internet | Data downloaded. Logger removed | REMOVED | REMOVED | REMOVED
1 | [9 empty] | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17
0
Note on W2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Check Enviro performance sheet vs Arup pre-site sheet vs Enviro install sheets
Note on AB2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Take notes from relevant tab on Enviro performance sheet - note any important bits of info such as silt, ragging, monitor issues, unable to access, unable to obtain data
Note on W3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Has the monitor been installed in the correct manhole? Check MH ref, location and W3W
Note on X3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Has the monitor been installed in the correct pipe? A, B - incoming or X, Y - outgoing
Note on Y3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Does the pipe size match between performance sheet, pre-site sheet, install sheet and GIS? Are there any big discrepancies that need highlighting to FS contractor?
Note on Z3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Does the pipe shape match between performance sheet, pre-site sheet, install sheet and GIS? Are there any discrepancies that need highlighting to FS contractor?
Note on AB9: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Loose sensor - refitted, okay in later interims
Note on AE35: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Monitor relocated to X pipe
Note on AF38: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Monitor relocated to X pipe
Note on AE69: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Sensor blown and reinstalled - can now be removed
Note on AF70: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Monitor relocated to X pipe
Note on AB73: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: FM blown out twice during Interim 1 and 4. Subsequently relocated to X pipe.
Note on AE73: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: FM blown out twice during Interim 1 and 4. Subsequently relocated to X pipe.
Note on AF73: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Monitor relocated to X pipe
Note on AF119: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Sensor blown out and removed
Note on AF120: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Sensor blown out and removed
Note on AC130: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Sensor dismounted from pipe, refitted - okay since
Note on AF146: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Sensor blown out and removed
Note on AF148: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Sensor blown out and removed

## Weekly quality check
| Comment on: Data quality, volume balance, drift (inspect previous data), scattergraphs, reaction to rainfall, site remedies carried out by contractor. Upon completion of data checks look at previous weeks and consider if actions are required. Actions may include sending the contractor an email or having a phone call regarding data quality to understand what could be done to improve. This may include upgrading a monitor/moving a monitor. Any actions sent to the contractor must be logged in the communications log tab. | [6 empty] | .
| Interim 1 |  |  | Interim 2 |  |  | Interim 3 |  |  | Interim 4 |  |  | Interim 5 |  |  | Interim 6 |  |  | Interim 7 |  |  | Interim 8 |  |  | Interim 9 |  |  | Interim 10 |  |  | Interim 11 |  |  | Interim 12
FM / DM / PL | Silt (mm) | COMMENT | Actions | Silt (mm) | COMMENT | Actions | Silt (mm) | COMMENT | Actions | Silt (mm) | COMMENT | Actions | Silt (mm) | COMMENT | Actions | Silt (mm) | COMMENT | Actions | Silt (mm) | COMMENT | Actions | Silt (mm) | COMMENT | Actions | Silt (mm) | COMMENT | Actions | Silt (mm) | COMMENT | Actions | Silt (mm) | COMMENT | Actions | Silt (mm) | COMMENT | Actions
FM01 |  | Telemetry download. Poor data - depths all below 0.05m (some negative depths recorded). Velocities better but spiky data. No flows recorded in normal conditions and very minor storm response recorded. Alt: Any MH US or DS e.g. 8703 or 8801 US | Check Interim 2 data. |  | Site visit not completed, unable to download telemetry data. |  |  | Poor data - depths all below 0.05m (some negative depths recorded).No flow recorded in normal flow conditions.Velocity values are spiky.Wide scatter.Sensor cleaned from ragging. | Query with Enviromontel |  | Poor data, wide scatter. Very low readings of flow velocity and depth (often below 0.05m). No recorded data since the early hours of the 4th Sept | Query with Enviromontel |  | As per previous interim Trickle flow Enviromonetel Response: 2 man crew this week - manual checks to take place next week | Query with Enviromontel |  | Removal Requested 19/09 | Query with Enviromontel |  | Good data available until 25th Sept. Monitor now noted to have been moved.
FM02 |  | No data until 09/08/2024. Data from 09/08/2024 seems ok, diurnal profile recorded. Flows responsive to rainfall. Scatter plot looks good. DWF seems low - possibly under-recorded. | Obtain week 1 data. |  | Good data, close scatter, diurnal profile evident, storm response evident. |  |  | Site visit required - unit does not dial in through the internet |  |  | Good data, diurnal profile and storm response evident. Close scatter |  |  | Okay |  |  | Removal Requested 19/09 |  |  | Data available until 20th Sept. Monitor now noted to be moved.
FM03 |  | Very low flows recorded in DWF (small catchment area upstream). Flows responsive to storms. Depth data tends to drift. |  |  | Site visit not completed, unable to download telemetry data. |  |  | Data downloaded.Very low flow recorded in DWF.Responsive to storm events.Depth values drift upwards. | Query wiyth Environmental |  | Site visit required - unit does not dial in through the internet. No data since 30th August | Query with Enviromontel |  | No Data Enviromontel Response: Monitor to be swapped on site this week |  |  | Negative depth values from 04/09/2024.Sensor cleaned from ragging. Graph showed calibration error - Sensor recalibrated. | Query with Enviromontel |  | Depth values appear better after calibration. Very low flow readings in recent data. Sensor cleaned |  |  | Very poor data | Leave in for winter flows (linked to SOIMP) |  | Continued poor data |  |  | Continued poor data. |  |  | Continued poor data.
FM04 |  | Good data. Diurnal profile evident. Flows responsive to rainfall. Scatter plot looks good. |  |  | Site visit not completed, unable to download telemetry data. |  |  | Good data. Diurnal profile evident. Flows responsive to rainfall. Scatter plot looks good.Responsive to rainfall.Sensor cleaned from ragging |  |  | Good data. Diurnal profile evident. Flows responsive to rainfall. Scatter plot looks good.Responsive to rainfall.Sensor cleaned from ragging |  |  | Okay Steady flow, sensor cleaned from ragging and grease. |  |  | Data looks good.Sensor clear but wiped anyway. |  |  | Good data, good scatter, diurnal and storm response. Sensor cleaned. |  |  | Good Data. Makes sense with d/s FM155. | Leave in for winter flows (linked to SOIMP) |  | Generally good data - some velocity drop out during storm event. Makes sense with d/s FM155. |  |  | Good data. |  |  | Good data.
FM05 |  | FM on secondary leg of bifurcation - no flow recorded. Tiny response to storm event. |  |  | Site visit not completed, unable to download telemetry data. |  |  | FM is located in secondary leg of bifurcation.Tiny amount of flow recorded during storm events.Sensor clear but wiped anyway |  |  | Small amount of flow during storm events. Sensor cleaned. Wide scatter |  |  | Trickle flow. Responds during storm events. Wide scatter |  |  | Poor data.Negative depth values.Dry pipe. Sensor cleaned from ragging.Wide scatter.Tiny amount of flow recorded during storm events. |  |  | Poor data, some negative depth values previously. Very low flow, more flow in storm events |  |  | Bifurcation - minor spills recorded. | Leave in for winter flows (linked to SOIMP) |  | Bifurcation - minor spills recorded. |  |  | Bifurcation - no spills. |  |  | Bifurcation - no spills.
FM06 |  | Very poor data. No depths recorded until 09/08/24, and look unreliable after that. No velocities recorded in DWF. Contractor states "Loose sensor cleaned and refitted to ring". | Check with contractor that refitting sensor will improve data. |  | Site visit not completed, unable to download telemetry data. |  |  | Data downloaded.Poor data.No velocities recorded at DWF.Responsive to rainfall.Sensor cleared from debris and cleaned from grease. | Query wiyth Environmental |  | No velocity recorded during DWF. Responds to rainfall | Query with Enviromontel |  | Okay. Slow flow, sensor cleaned from ragging |  |  | Monitor removed and relocated. See FM155 |  |  | See FM155
FM09 |  | Data not retrieved. |  |  | Good depth data, velocities regularly drop out. | Query with Enviromentel |  | Telemetry data downloaded.Data looks good.Responsive to rainfall.Diurnal profile evident.Velocity drops down at some places.Velocity drops down at storm events.Evidence of surcharge.Scattergraph looks resonable. | Query with Enviromontel |  | Telemetry data downloaded.Data looks good.Responsive to rainfall.Diurnal profile evident.Velocity drops down at some places.Velocity drops down at storm events.Evidence of surcharge.Scattergraph looks resonable. No data past 2nd sept due to download? | Query with Enviromontel |  | No Data. | Query with Enviromontel |  | Velocities dropped out from 11/09, probably due to ragging. | Query with Enviromontel |  | No data since 19th sept | Query with Environmentel |  | Good Data. Makes sense with d/s FM10. | Leave in for winter flows (linked to SOIMP) |  | No data since 01/10 - site notes state site visit required |  |  | Good data. Surcharged during storm. |  |  | Good data. Surcharged during storm.
FM10 |  | Data not retrieved. |  |  | Good data, scatter and graphs show evidence of surcharging in storm events, diurnal profile evident, storm response evident. |  |  | Site visit required - unit does not dial in through the internet |  |  | Good data, scatter and graphs show evidence of surcharging in storm events, diurnal profile evident, storm response evident. No data beyond 2nd Sept due to download? |  |  | No Data. | Query with Enviromontel |  | Good data |  |  | No data since 17th sept | Query with Environmentel |  | Good Data. Makes sense with d/s FM09. | Leave in for winter flows (linked to SOIMP) |  | Sudden drop in velocity data on 02/10, monitor significantly under-reading after this date when compared to rest of FS period. | Query with Environmentel |  | Good data. Surcharged during storm. |  |  | Good data. Surcharged during storm.
FM11 |  | Data not retrieved. |  |  | Close scatter, good storm response. No flows recorded apart from in storm events (d/s of bifurcation - likely high level pipe) |  |  | Site visit required - unit does not dial in through the internet |  |  | Close scatter, good storm response. No flows recorded apart from in storm events (d/s of bifurcation - likely high level pipe). No data beyond 2nd sept due to download? |  |  | No Data. | Query with Enviromontel |  | Bifurcation - only spills recorded. |  |  | Only has data on spills but possibly missing latest spill data? |  |  | Good data. Bifurcation - records no DWF but reacts to rainfall. | Leave in for winter flows (linked to SOIMP) |  | Bifurcation - only spills during rainfall, does not appear to have operated during latest interim. |  |  | Bifurcation - operates during storm events. |  |  | Bifurcation - operates during storm events.
FM13 |  | Data not retrieved. |  |  | Good storm response, no diurnal pattern observed due to standing water. Good scatter and volume balance. |  |  | Site visit required - unit does not dial in through the internet |  |  | Good storm response, no diurnal pattern observed due to standing water. Good scatter and volume balance. Good storm response. No data beyond 2nd sept due to download? |  |  | No Data. | Query with Enviromontel |  | No DWF recorded. Some storm response. |  |  | No data since 17th sept | Query with Environmentel |  | Velocity drop outs. Slow flow, pipe nearly at full bore. Good data during storms and matches well with u/s FM16. | Leave in for winter flows (linked to SOIMP) |  | Good depth data, velocity drops out but good during storms. |  |  | FM16 > FM15 > FM13. FM16 and FM13 match well wrt flows but FM15 records much less flow. |  |  | Good data. Surcharged during storm.
FM14 |  | Telemetry download. 4 days of data available. Very low flows - small catchment upstream. Small response to rainfall. Wide scatter. Unlikely to get better data elsewhere due to small u/s catchment. |  |  | Very low flows due to small catchment, small correlation on scatter graph. Response to rainfall. Ragging and low flows appear to have affected velocity. |  |  | Site visit required - unit does not dial in through the internet |  |  | No readings beyond 22nd August | Query with Enviromontel |  | Very low flows due to small catchment. Response to rainfall |  |  | Very low flow. Sensor cleaned from ragging. |  |  | Data ok, responsive to storm events. |  |  | Site visit required - unit does not dial in through the internet | Leave in for winter flows (linked to SOIMP) |  | Data okay during storms, data quality matches previous interims. |  |  | Very low flows. |  |  | Low flows. | Remove?
FM15 |  | Telemetry download. 4 days of data available. Low flows. Small response to rainfall. Wide scatter. U/S FM16 records much higher peak flows, however there is a CSO between the two. |  |  | Good data, diurnal profile evident and some storm response. Wide scatter. |  |  | Site visit required - unit does not dial in through the internet |  |  | No readings beyond 22nd August | Query with Enviromontel |  | Low flows, delayed response to rainfall? Slow flow sensor cleaned |  |  | Low flows. Negative depth values. Sensor cleaned from ragging. Good data from 13/09. |  |  | Low flows and negative depth values. Good diurnal pattern and storm response. |  |  | Unable to access. Parked cars blocking room for setup | Leave in for winter flows (linked to SOIMP) |  | Low flows and negative depth values. Good diurnal pattern and storm response. |  |  | FM16 > FM15 > FM13. FM16 and FM13 match well wrt flows but FM15 records much less flow. Poor data at this monitor. |  |  | Poor data | Remove?
FM16 |  | Telemetry download. 4 days of data available. Minimal flows in DWF. Good storm response. Scatter plot looks reasonable. Peak flows significantly decrease at d/s FM15, however there is a CSO between the two. |  |  | Good scatter graph. Limited depth and flow storm response. Good diurnal and storm response in velocity. Good volume balance. |  |  | Telemetry data downloaded.Poor data.Data drops down from 17/08/2021-22/08/2021 and from 27/08/2021.Limited storm response.Diurnal profile is evident.Wide scatter.Depth is showing negative values. | Query with Enviromontel |  | Data Ok. Diurnal profile evident and storm response. Depth still shows negative values. SCatter ok. | Query with Enviromontel |  | Negative depths. Low flows Fast flows, sensor cleaned | Query with Enviromontel |  | Negtive depth values. Low flows. Sensor cleaned from ragging. Sensor recalibrated to match manual measurements. |  |  | Ok data, diurnal pattern and storm response. |  |  | Good data. matches well with d/s FM13. | Leave in for winter flows (linked to SOIMP) |  | Good velocity data, good depth during storms but some negative values during dry weather. |  |  | FM16 > FM15 > FM13. FM16 and FM13 match well wrt flows but FM15 records much less flow. |  |  | Poor data from 18/10 - depths drop below 0. | Raise with Enviromontel
FM17 |  | Telemetry download. 4 days of data available. Poor data for first 3 days. Velcoities and depths jump up on 08/08/24. Need more data to assess quality. |  |  | No flow or velocity data since previous download. | Query with Enviromentel |  | Site visit required - unit does not dial in through the internet |  |  | Data Ok. Diurnal profile evident and storm response. Depth still shows negative values. SCatter ok. |  |  | Low flows, responds to rainfall. Slow flow, sensor cleaned from heavy ragging- see photos. Wide Scatter. |  |  | Site visit required - unit does not dial in through the internet | Query with Enviromontel |  | ok data, wide scatter, responsive to storm events but low flow |  |  | Good depth data, average/poor velocity data. Monitor removed. | Removed
FM18 |  | Telemetry download. 4 days of data available. Located on spill pipe - no flows in DWF. Minor storm response on 05/08/2024 |  |  | Located on spill pipe - flows only evident after storm event. |  |  | Site visit required - unit does not dial in through the internet |  |  | No data since 22nd Aug | Query with Enviromontel |  | Located on spill pipe - 1no spill evident after storm event. |  |  | Site visit required - unit does not dial in through the internet | Query with Enviromontel |  | On spill pipe, only flow in storm event |  |  | Good data - spills recorded. Telemetry downloaded, to be removed on next site visit | To be removed
FM19 |  | Telemetry download. 4 days of data available. Data looks reasonable quality. Minimal DWF due to small u/s catchment but diurnal profile evident. Flows respond to rainfall. |  |  | Minimal DWF due to small US catchment but profile evident along with storm response. Good scatter. |  |  | Site visit required - unit does not dial in through the internet |  |  | No data since 22nd Aug | Query with Enviromontel |  | Okay |  |  | Removal Requested 19/09 |  |  | Good data up to 25th Sept. Monitor now noted to be moved.
FM20 |  | Data not retrieved. |  |  | Storm response evident, no diurnal trend as on spill pipe of CSO. Good scatter. |  |  | Site visit required - unit does not dial in through the internet |  |  | Storm response evident, no diurnal trend as on spill pipe of CSO. Good scatter. |  |  | No Data | Query with Enviromontel |  | Removal Requested 19/09 |  |  | No data since 12th Sept. Monitor noted to have been relocated
FM21 |  | Telemetry download. Good data quality. Clear diurnal profile and strong storm response. Close scatter with evidence of surchrage. Unable to check volume balance - data not available at u/s monitor, poor data at d/s monitor. |  |  | Good data, good scatter, good volume balance. Diurnal profile and storm response, evidence of surcharge during storms. |  |  | Telemetry data downloaded.Good data.Scatter graph looks good.Diurnal profile and storm response.Velocity drops down during storm events.Evidence of surcharge. |  |  | Good data, good scatter, good volume balance. Diurnal profile and storm response, evidence of surcharge during storms. |  |  | Okay |  |  | Data looks good. Velocities affected by ragging from 16/09 - cleaned. |  |  | No data since 17th Sept | Query with Environmentel |  | Good data.. Monitor removed. | Removed
FM22 |  | No data for 1.5 days at start. Depth data looks good following this. Velocity data drops out on 08/08/24. Sensor cleaned from ragging. | Check Interim 2 for repeat ragging issues. |  | Storm response evident. Good depth data. Multiple velocity drop outs. |  |  | Velocity data drops at multiple times.Poor scatter.Depth data drops to zero multiple times.Sensor cleaned from ragging. | Query wiyth Environmental |  | Velocity data drops at multiple times.Poor scatter.Depth data drops to zero multiple times.Sensor cleaned. Storm response | Query with Environmental |  | No velocity for majority of interim | Query with Enviromontel |  | Removal Requested 19/09 |  |  | Depth data ok, no flow or velocity data since 5th sept. Monitor noted to now be moved.
FM23 |  | Data not retrieved. |  |  | Flow and velocity data dropped out. Depth data shows small amount of diurnal profile and storm response. | Query with Enviromentel |  | Site visit required - unit does not dial in through the internet |  |  | Drift in flow and velocity data. Storm response evident, some diurnal pattern. No data since 2nd Sept, times appear wrong in sensor (also in site notes). | Query with Environmental |  | Okay Steady flow, sensor cleaned from ragging. Sensor is offset. |  |  | Data looks good. No data after 18/09/2024 |  |  | Ok data, wide scatter. Responsive to storm events and diurnal profile evident. Calibrated. |  |  | Site visit required - unit does not dial in through the internet | Leave in for winter flows (Catchment FM) |  | Good data - slow response evident in velocity data. |  |  | Good data. |  |  | Velocity drops out at end of period. Sensor cleaned.
FM24 |  | Telemetry download. Small upstream catchment. No / minimal flow recorded in DWF. Minor storm response. |  |  | Minimal DWF due to small US catchment, storm response evident. Medium scatter. |  |  | Telemetry data downloaded.Data looks good.Minimal DWF due to small upstream area of the catchment.Responsive to stormn events.Evidence of diurnal profile.medium scatter. |  |  | Diurnal profile and storm response evident. Ok scatter. Very low volumes and depths due to small US catchment |  |  | Okay. Minimal DWF due to small upstream area of the catchment. Responsive to storm events.Evidence of diurnal profile |  |  | Removal Requested 19/09 |  |  | Data ok, data up to 17th sept. Monitor now noted to be moved
FM25 |  | Data looks reasonable. Diurnal profile evident in DWF. Flows respond to rainfall. Medium scatter. Pump profile evident from 11/08/24. |  |  | Response to storms, some diurnal profile but pump profile evident mostly from 11/08 onwards. Good scatter |  |  | Pumped flow.Responsive to storm events.No data from 27/08/2021.Scattergraph looks reasonable.Steady flow. Sensor cleaned from ragging. |  |  | No data since 2nd sept. Storm response evident. Good scatter |  |  | Okay |  |  | Removal Requested 19/09 |  |  | Recent data seems different to the rest of the data. Data ok, dirunal response evident. Notes state monitor now moved.
FM26 |  | Telemetry download. Depths look ok, velocities drop out in places. Diurnal profile evident in DWF. Flows respond to rainfall. Medium scatter. Pump profile evident in flow from 11/08/24. Volume balance with u/s FM24 and FM25 is ok for first storm but not for second due to data drop outs. |  |  | First half of data responds to storms, second half there is more evidence of diurnal flow and predominant pump profile evident. Good scatter |  |  | Telemetry data downloaded.Pumped flow.Responsive to rainfall.Good scatter. |  |  | Diurnal profile and storm response evident. Scatter ok. |  |  | Okay |  |  | Removal Requested 19/09 |  |  | Recent data seems lower quality. Noted that monitor now moved.
FM27 |  | Telemetry download. Data looks reasonable. Low flows in DWF. Good storm response. Close scatter. |  |  | Site visit not completed, unable to download telemetry data. |  |  | Telemetry data downloaded.Data looks good.Low flows in DWF.Responsive to storm events.Diurnal profile s evident. |  |  | Diurnal profile and storm response evident. Scatter ok. |  |  | No Data | Query with Enviromontel |  | Site visit required - unit does not dial in through the internet | Query with Enviromontel |  | No data since 5th Sept. | Query with Environmentel |  | Good data. Monitor removed. | Removed
FM28 |  | Good data. Diurnal profile evident. Flows responsive to rainfall. Scatter plot looks good. Volume balance ok. |  |  | Good data. Diurnal profile and storm response evident. Good scatter and volume balance. |  |  | Data looks good.Diurnal profile is evident.Scattergraph looks good.Responsive to storm events.Sensor cleaned from ragging. |  |  | Data looks good.Diurnal profile is evident.Scattergraph looks good.Responsive to storm events.Sensor cleaned from ragging. |  |  | No Data | Query with Enviromontel |  | Removal Requested 19/09 |  |  | Good data with diurnal profile and storm response. Step up in recent depth data. Monitor noted to now be moved.
FM29 |  | Telemetry download. 4 days of data available. Data looks reasonable quality. Diurnal profile evident in DWF. Good storm response. Medium scatter. |  |  | Good data. Diurnal profile and storm response evident. Good scatter and volume balance. |  |  | Telemetry data downloaded.Data looks good.Responsive to storm events.Diurnal profile is evident.Scattergraph looks good. |  |  | Telemetry data downloaded.Data looks good.Responsive to storm events.Diurnal profile is evident.Scattergraph looks good. |  |  | Okay |  |  | Telemetry data downloaded. Velocities affected by ragging from 16/09. | Query with Enviromontel |  | Good data since cleaned sensors with diurnal profile and storm response. |  |  | Good data | Leave in for winter flows (Catchment FM) |  | Good data |  |  | Good data. Evidence of slow response. |  |  | Good data. Evidence of slow response.
FM30 |  | Telemetry download. 4 days of data available. Very low flows in DWF (relatively small u/s catchment). Some storm response. Generally quite poor data (outgoing pipe). Alt: Any MH DS, alts may be in gardens so possibly 0706 is best. | Relocate |  | Site visit not completed, unable to download telemetry data. |  |  | Very low flow recorded in DWF.Responsive to storm events.Depth values drift upwards.Sensor cleaned from ragging |  |  | No data since 29th August | Query with Environmental |  | Okay Slow flow, sensor cleaned |  |  | Site visit required - unit does not dial in through the internet | Query with Enviromontel |  | Good data, diurnal flow and storm response evident. Low flows |  |  | Monitor removed. | Removed
FM31 |  | Small u/s catchment. Minimal DWF recorded. Good storm response. Close scatter. |  |  | Minimal DWF due to small US catchment, storm response evident, good scatter. |  |  | Small upstream catchment.Minimal DWF recorded.Responsive to storm events.Scattergraph looks good.Sensor cleaned from ragging |  |  | Small upstream catchment.Minimal DWF recorded.Responsive to storm events.Scattergraph looks good.Sensor cleaned from ragging |  |  | Okay |  |  | Low flow. Sensor cleaned from ragging. |  |  | Good data, diurnal flow and storm response evident. Low flows |  |  | Left in to gather more data from reloacted FM156. Good data. | Remove
FM32 |  | Poor data. Depths all below 0.06m. No DWF recorded. Some storm response. Scattergraph shows little to no correlation. Alt: No clear alt without missing flows from one of two incoming lines to installed MH. Would need 2nd FM to cover both lines. | Relocate |  | Poor data, Some small amounts of storm response but little DWF profile. Depths in negative numbers and poor scattergraph correlation. | Query with Enviromentel |  | Poor data.Depth data is showing negative values.Responsive to some storm events.Poor scattergraph.Sensor cleaned from ragging | Query with Enviromontel |  | Poor data.Depth data is showing negative values.Responsive to some storm events.Poor scattergraph.Sensor cleaned from ragging | Query with Enviromontel |  | Okay Steady flow, installed in X pipe, sensor cleaned. |  |  | Monitor relocated to FM156 |  |  | See FM156 | [8 empty] | Data downloaded. Monitor removed
FM33 |  | Telemetry download. 4 days of data available. FM located on spill pipe - no DWF, minor storm response. |  |  | Located on spill pipe - no DWF profile evident, some small storm response. |  |  | FM is located in spill pipe.No DWF.Some storm response.Sensor clear but wiped anyway. |  |  | FM is located in spill pipe.No DWF.Some storm response |  |  | Okay |  |  | Okay.FM located on spill pipe |  |  | Okay data, located on spill pipe |  |  | Left in to gather more data from reloacted FM156. Good data - records spills. | Remove |  | To be removed |  |  | Data downloaded. Monitor removed
FM34 |  | No data recorded for first 2 days. Velocity data shows diurnal profile and storm response. Depth data looks unreliable. Wide scatter. Alt: Numerous alts US and DS e.g. 9208 or 9201. | Relocate |  | Diurnal profile evident and storm response. Scatter graph has wide spread. |  |  | Depth data showing negative values.Responsive to storm events.Diurnal profile is evident.Wide scatter.Sensor clear but wiped anyway. | Query with Enviromontel |  | Depth data showing negative values.Responsive to storm events.Diurnal profile is evident.Wide scatter.Sensor cleaned from ragging | Query with Enviromontel |  | Negative depths Fast flows, very greasy pipe - sensor cleaned. Enviromonetel Response: Awaiting DWCC Approval on relocations | Relocating? |  | Monitor removed and relocated to FM157 |  |  | See FM157
FM35 |  | Not provided. | Request from contractor |  | Good velocity data. Depths recording negative values up until 18/08. | Query with Enviromentel |  | Telemetry data downloaded.Good velocity data. |  |  | Good data, depth data seems to have improved and is no longer negative. Good scatter |  |  | Okay Sensor relocated to X pipe - see site check sheet for information. |  |  | Monitor relocated to FM158 |  |  | See FM158
FM37 |  | Telemetry download. Poor data - messy - no evidence of diurnal profile or storm response. Located on outgoing pipe. Scatter plot shows no correlation. Alt: only 1no. MH as alt available 4109. | Relocate |  | Poor correlation on scatter. Some amount of diurnal profile but limited storm response. |  |  | Telemetry data downloaded.Poor data.No storm respose.Some amount of diurnal profile.Poor scatter. | Query with Enviromontel |  | Poor correlation on scatter. Some amount of diurnal profile but limited storm response. Pronounced response to most recent storm likely resultant from exceptional conditions (high tide and significant storm) |  |  | Okay |  |  | Okay. |  |  | Good data, ok scatter. Diurnal profile and storm response evident |  |  | Good data. Monitor removed. | Removed
FM38 |  | Located d/s of SPS - pump profile evident. Good storm response. Data and scatter plot look good. Volume imbalance with d/s FM41 | Check with contractor about volume imbalance. |  | Pump profile evident, some storm response. Scatter plot good. |  |  | Pumped flow.No storm response.Wide scatter.Sensor cleaned from ragging. |  |  | Pumped flow. Some storm response on larger storms.Wide scatter.Sensor cleaned from ragging. |  |  | Okay Steady flow, sensor cleaned. Pipe size 400mm Enviromonetel Response: Checks carried out please see site check sheet for interim 5 |  |  | Removal Requested 19/09 |  |  | Good data up to 23rd septh. Monitor now moved.
FM39 |  | Fast flow. Poor data for first 3.5 days, including first storm event. Depths and volumes improve after second storm event. Located d/s of a PS - pump profile evident. Fairly close scatter plot for data after second storm event. Volume imbalance with d/s FM40. Flows reduce by about half during DWF. | Check with contractor about volume imbalance. |  | Pumped flow.Located d/s of SPS.Evidence of diurnal profile.Responsive to storm events.Scattergraph looks good. On 15/08, depths suddenly drop down. |  |  | Pumped flow.Responsive to storm events.Depth showing negative values.Evidence of diurnal profile.Sensor cleaned from ragging. | Query with Enviromontel |  | No normal data since 28th August | Query with Enviromontel |  | No depth data Fast erratic flow, sensor ring blown out on arrival - refitted. Pipe size 375mm. Enviromonetel Response: Checks carried out please see site check sheet for interim 5 | Query with Enviromontel |  | Removal Requested 19/09 |  |  | Good data up to 24th sept. Monitor now moved.
FM40 |  | Located d/s of SPS - pump profile evident. Evidence of diurnal profile. Good storm response. Close scatter. Volume imbalance with u/s FM39. | Check with contractor about volume imbalance. |  | Pumped flow.Located d/s of SPS.Evidence of diurnal profile.Responsive to storm events. |  |  | Pumped flow.Responsive to storm events.Good scatter.Evidence of diurnal profile.Sensor cleaned from ragging. |  |  | Pumped flow.Responsive to storm events.Good scatter.Evidence of diurnal profile.Sensor cleaned from ragging. |  |  | Okay Fast flow conditions, sensor cleaned - data downloaded Enviromonetel Response: Checks carried out please see site check sheet for interim 5 |  |  | Removal Requested 19/09 |  |  | Good data up to 23rd sept. Monitor now moved.
FM41 |  | Located d/s of SPS - pump profile evident. Evidence of diurnal profile. Good storm response. Close scatter. Volume imbalance with u/s FM38. | Check with contractor about volume imbalance. |  | Pumped flow.Located d/s of pumping station.Evidence of diurnal profile.Responsive to storm events.Close sactter.Volume imbalance with flow monitor u/s FM38 | Check with contractor about volume imbalance. |  | Pumped flow.Responsive to some storm events.Volume imbalance with flow monitor u/s FM38.Sensor cleaned from ragging. | Checkwith contractor about volume imbalance. |  | Pumped flow, small response to storm events. Possible volume imbalance with US monitor FM38. Cleaned from ragging |  |  | Okay Steady flow, sensor cleaned. Pipe size 300mm Enviromonetel Response: Checks carried out please see site check sheet for interim 5 |  |  | Removal Requested 19/09 |  |  | Good data up to 23rd sept. Monitor now moved.
FM42 |  | Telemetry download. 4 days of data available. Good data. Close scatter. Diurnal profile evident and good storm response. |  |  | Good data.Close scatter.Responsive to storm events.diurnal profile is evident. |  |  | Site visit required - unit does not dial in through the internet |  |  | No data since 22nd Aug | Query with Enviromontel |  | Okay Fast flows, sensor cleaned |  |  | Removal Requested 19/09 |  |  | Good data up to 25th sept. Monitor now moved.
FM43 |  | Telemetry download. 4 days of data available. Depths look ok but no velocity data recorded. Installed in outgoing pipe. Alt: 1no. MH US 2401 otherwise use DS 1401 but they inlcude couple houses and potentially road. | Relocate |  | Poor data.Velocity data was recorded for only two days during the survey. The rest of the days have no velocity data.Depth value drops to zero during one of the storm event.Depths drop out on 19/08. | Query with Enviromontel |  | Site visit required - unit does not dial in through the internet |  |  | Very poor data quality. No trends evident. Notes of silt and incorrect time. | Query with Enviromontel |  | Velocity drops out during storms Enviromonetel Response: Please see site check sheet from interim 4 before and after sensor clean photos - evidencing poor data | Query with Enviromontel |  | Removal Requested 19/09 |  |  | ok data to 23rd sept. Monitor now moved.
FM44 |  | Good data. Very close scatter. Evidence of surcharge. |  |  | Good data.Very close scatter.Responsive to rainfall events.Evidence of surcharge. |  |  | Data looks good.Responsive to storm events.Evidence of surcharge.Scattergraph looks good.Sensor cleaned from ragging |  |  | Good data, diurnal patter and storm response evident. Evidence of surcharge in storm events. No checks completed. |  |  | Okay |  |  | Removal Requested 19/09 |  |  | Good data to 25th sept. Monitor now moved.
FM45 |  | Telemetry download. Good depth data, velocities affected by ragging in places. Evidence of diurnal profile and storm response. |  |  | Telemetry downloaded.Responsive to storm events.diurnal profile evident.Velocity affected by ragging in places. |  |  | Telemetry data downloaded.Responsive to storm events.Velocity affected by ragging in places.Evidence of diurnal profile. |  |  | Diurnal pattern evident, responsive to storm events. Possible surcharge |  |  | Velocity drops out during storms | Query with Enviromontel |  | Okay |  |  | Diurnal pattern evident, responsive to storm events. Possible surcharge and drifts in data? |  |  | Good data. Velocity drop out towards end of interim. | Report ot Enviromontel |  | Poor data during interim, data drop out throughout and poor velocity response during storm (06/10), depth data okay. |  |  | Velocity drop out at start of interim but improves after this. Evidence of surcharge during storm on 16/10. Evidence of slow response |  |  | Reasonable data, evidence of slow response, surcharge and back flow.
FM47 |  | Telemetry download. 4 days of data available. Depths look ok but no velocity data recorded. Alt: no clear alt, only MHs DS that have incoming lines between. | Relocate |  | Poor data.Depths look ok.Velocity values not recorded | Query with Enviromontel |  | Poor data.Velocity values are not recorded.Depth values looks ok.Sensor cleaned from silt. | Query with Enviromontel |  | Poor data quality, no flow or velocity data. Seem to be steps in depth data too. | Query with Enviromontel |  | No velocity data Slow flow, sensor and monitor swapped. Sensor installed offset. | Query with Enviromontel |  | Removal Requested 19/09 |  |  | Erratic flow and velocity data. Monitor now moved.
FM48 |  | Telemetry download. 4 days of data available. Very low flows and depths. Reasonable scatter. Very small u/s catchment |  |  | Telemetry downloaded.Flow is very low.Responsive to storm events.Very small u/s catchment.Sensor cleaned from grease. |  |  | Data downloaded.Flow is very low.Depth values are very low.Responsive to storm events.Sensor cleaned from ragging. |  |  | Flow and depth values very low. Evidence of diurnal profile and response to storm events. Good scatter |  |  | Okay |  |  | Very low flow and depth values.Depth showing negative values |  |  | Very low flow and depth values.Depth showing negative values. Good scatter |  |  | Telemtry data downloaded. To be removed. | To be removed |  | Removed
FM49 |  | Depths ok, velocities affected by ragging. Reasonable scatter. Diurnal profile and storm response evident. |  |  | Data looks good.Reasonable scatter.Responsive to storm avents.diurnal profile is evident. |  |  | Telemetry data downloaded.Data looks good.Responsive to storm events.Evidence of diurnal profile.Scattergraph looks good. |  |  | Good data and scatter graph. Dirunal profile and reponse to storm events |  |  | No Data | Query with Enviromontel |  | Good data |  |  | Good data, ok scatter. Diurnal profile and storm response evident |  |  | Good data. | Leave in for winter flows (Catchment FM) |  | Good data. |  |  | Good data. |  |  | Good data. Fast flow.
FM50 |  | Telemetry downloaded. Monitor located u/s of SPS - affected by on/off levels of pumps. |  |  | Pumped flow.Monitor located u/s of SPS. |  |  | Site visit required - unit does not dial in through the internet |  |  | No data since 20th August | Query with Enviromontel |  | No Data | Query with Enviromontel |  | Removal Requested 19/09 |  |  | No data since 17th Sept. Monitor now moved
FM51 |  | Data quality looks good.Scattergraph looks good.Responsive to rainfall. Sensor cleaned from ragging. |  |  | Good data.Scattergraph looks good.Responsive to rainfall.diurnal profile is evident.Sensor clear but wiped anyway. |  |  | Good data. |  |  | Good data.Sensor claned from ragging |  |  | Good data, none since the 9th Sept |  |  | Good data, small flow that follows storm events and has a diurnal pattern. |  |  | Data looks good.Storm respnse and diurnal profile is evident. |  |  | Good data. | Leave in for winter flows (Catchment FM) |  | Good data for most of interim - some possible data drop out towards end? To be checked next interim. |  |  | Velocity drop outs. Sensor cleaned. |  |  | Good data.
FM54 |  | Telemetry download. Flow monitor located on spill pipe.No flow recorded.Responsive to only one storm event. |  |  | Telemetry downloaded.Flow monitor is located at spill pipe.Responsive to only on storm event.Velocity is showing negative values. |  |  | Spill pipe - responsive to two storm events across full period. |  |  | FM located on spill pipe.Depth showing negative values.Responsive to only few storm events. |  |  | FM located on spill pipe.Depth showing negative values.Responsive to only few storm events. |  |  | No flow, FM located on spill pipe. |  |  | No flow, FM located on spill pipe. |  |  | Telemtry data downloaded. To be removed. | To be removed |  | Removed
FM55 |  | Very low flow conditions due to monitor location.Only very small catchment upstream.Responsive to only one storm event. |  |  | Very low flow conditions. Only very small catchment area upstream. Responsive to only one storm event. Velocity drops to zero sometimes. |  |  | Low flows - small u/s catchment. |  |  | Very low flows.Small upstream catchment.Minor storm response.No data after 04/09/2024.Depth showing negative values.Sensor cleared of ragging |  |  | Very low flows due to small upstream catchment. Some storm response but little diurnal pattern. Some depth values negative. Poor correlation. | Query with Enviromontel |  | Removal Requested 19/09 |  |  | Removed
FM56 |  | Telemetry downloaded. Low flow conditions due to small catchment upstream.Responsive to only one storm event. |  |  | Site visit not completed, unable to download telemetry data. |  |  | Reasonable data considering low flows (small u/s catchment) |  |  | Small u/s catchment.Low flows.Few storm responses.No data after 05/09/2024 |  |  | No data since 6th Sept | Query with Enviromontel |  | Removal Requested 19/09 |  |  | Removed
FM57 |  | Data quality looks good.Scattergraph looks good.Diurnal profile and storm response evident.Sensor cleaned from grease. |  |  | Telemetry data downloaded.Good data.Scattergraph looks good.Dirunnal profile is evident and responsive to storm events. |  |  | Velocities dropped out towards end of interim - needs cleaning. | Enviromontel to clean |  | Responsive to storm events.Diurnal profile is evident.Sensor cleared of ragging.Velocity and depth data drops out from 05/09/2024. | Query with Enviromontel |  | Diurnal pattern and storm reponse evident. Obvious step in readings after a previous cleaning. Good scatter. |  |  | Removal Requested 19/09 |  |  | Removed
FM58 |  | No data |  |  | Flow monitor located at one of the outgoing pipe of a bifurcation.No flow |  |  | No flow (bifurcation). |  |  | No flow(bifurcation) |  |  | No flow data at all and no depth or velocity data since 3rd Sept | Query with Enviromontel |  | Removal Requested 19/09 |  |  | Removed
FM59 |  | Says data downloaded, but none provided. |  |  | Telemetry data downloaded.Data looks good.Located at outgoing leg of bifurcation.Responsive to rainfall.diurnal profile is evident.Scattergraph looks good. |  |  | Good data. |  |  | Data looks good.Responsive to rainfall events.Diurnal profile is evident.Scattergraph looks good. |  |  | Good data, diurnal profile evident and responsive to rainfall. Good scatter. Possible drift in data towards latter end and some negative depths. | Query with Enviromontel |  | Good data, small flow that responds to storm events and velocity follows diurnal profile. |  |  | Good data.Responsive to storm events.Some negative depth values. |  |  | Good velocity data but very low depth data. Monitor to be removed. | To be removed |  | Removed
FM60 |  | Telemetry download. Located on storm sewer, no flow in DWF. Data quality is good.Scattergraph looks reasonable.Good storm response. |  |  | Sensor cleaned thoroughly from ragging. Data downloaded.Data looks good.Located on storm sewer.No flow in DWF.Responsive to raoinfall.Scattergraph looks good. |  |  | Storm sewer. Good data. |  |  | Storm sewer.No DWF.Responsive to rainfall.Data drop out from 30/08/2024.Sensor cleaned from ragging. |  |  | No data since 30th Aug | Query with Enviromontel |  | No flow, velocity responds to rainfall. |  |  | No DWF.Velocity responds to rainfall |  |  | Storm system, reacts to rainfall. To be removed. | To be removed |  | Removed
FM61 |  | Telemetry download. Very high velocity, very low depth. Depth and velocity data missing for first couple of days. No alternative sites. | Review in interim 2 |  | Data downloaded.Very high velocity and low depth.Depth values drops below zero.Velocities repsond to rainfall but depths too low for accurate reading. No alternative sites. |  |  | Poor - steep sewer. High velocities, low depths. No alternatives (all steep). |  |  | Poor data.High velocities and low depth value.Depth value drops below zero.Few storm responses. | FM to be Removed |  | Poor data, high velocities and low depths (below 0). Some storm response. No data since 9th Aug |  |  | Removal Requested 19/09
FM62 |  | Flow monitor located on spill pipe.No flow recorded. |  |  | Flow monitor located at spill pipe.No flow recorded. |  |  | Spill pipe - no flow. |  |  | FM in located at spill pipe.No flow. |  |  | No flow data recorded. Poor data. | Query with Enviromontel |  | Removal Requested 19/09
FM63 |  | Data looks good.Scattergraph looks reasonable.Diurnal profile is evident.Responsive to rainfall. |  |  | Data looks good.Wide scatter.Responsive to storm avents.diurnal profile is evident.Sensor cleaned from ragging. |  |  | Good data. |  |  | Good data.Responsive to storm events.Diurnal profile is evident.No data from 04/09/2023.Sensor cleaned from ragging. |  |  | No data since 4th Sept | Query with Enviromontel |  | Removal Requested 19/09
FM64 |  | Data looks good.Diurnal profile is evident.Responsive to rainfall. |  |  | Data looks ok.diurnal profile is evident.Responsive to rainfall.Close scatter.Sensor clear but wiped anyway. |  |  | Data ok. |  |  | Data looks ok.Few storm responses.Depth data drops below zero.Data drops from 04/09/2024.Sensor cleaned from ragging. |  |  | No data since 4th Sept | Query with Enviromontel |  | Removal Requested 19/09
FM65 |  | Poor data quality.Scattergraph looks good.Responsive to only one sorm event. Alt:D/S of 6003 | Relocate |  | Data looks ok.Scattergraph looks good.Depth value drops down multiple times.Gap in velicity recording.Responsive to few storm events. |  |  | Unable to download telemetry - site visit required. | Site visit required. |  | Data looks ok.Responsive to storm events.Depth value drops below zero multiple times. | Query with Enviromontel |  | No data since 4th Sept | Query with Enviromontel |  | No data since 4th Sept |  |  | Removed in error. Reinstalled on 25/09. | [5 empty] | Good data. |  |  | Good data. |  |  | Good data. Fast flow.
FM66 |  | Data looks good.Scattergraph looks good.diurnal profile is visible.Responsive to storm events. |  |  | Data looks good.Scattergraph looks good.diurnal profile is evident.Responsive to storm events.Sensor cleaned from ragging. |  |  | Velocities appear to be affeted by ragging at the end of the survey period. | Enviromontel to clean |  | .Responsive to storm events.Velocity and depths have dropped out towards the end of flow survey.Sensor cleared from grease. | Query with Enviromontel |  | Some evidence of diurnal flow and storm response although not as clear as before (possibly due to ragging?). Scatter ok. Sensor cleaned |  |  | Removal Requested 19/09 |  |  | Removed
FM67 |  | No data |  |  | Poor data.Depth value drops to zero from the mid of flow survey period.Wide scatter.Responsive to rainfall.diurnal profile is evident.Sensor cleaned from grease. | Query with Enviromontel |  | Velocities and depths have dropped out towards end of survey period. | Query with Enviromontel |  | Poor data.Velocities and depths have dropped out towards the end of survey period.Sensor cleaned from ragging. | Query with Enviromontel |  | Large step in depth data from 3rd-10th Sept before relocation, also possibly issue with flow data in this time. Some storm response. Sensor now on x pipe. |  |  | Negative depths recorded up to 10/09. FM was relocated to the X pipe on 10/09. Data improved. little/no flow and depth, however velocity follows diurnal profile, no data after midday 16/09 |  |  | See FM159
FM68 |  | Data looks good.Responsive to rainfall.Velocity drops down during storm events.Evidence of surcharge. |  |  | Telemetry data downloaded.Data looks good.Responsive to rainfall.Velocity drops down during storm events.Evidence of surcharge. |  |  | Reasonable data. |  |  | Data looks ok.Evidence of surcharge.Depth values drops below zero.Responsive to storm events. |  |  | Data ok, depth value drops below 0. Responsive to storm events but less evidence of diurnal profile. Evidence of some surge charge. No data since 9th Sept |  |  | Removal Requested 19/09 |  |  | Removed
FM69 |  | FM located on spill pipe - no DWF, minor storm response. |  |  | Flow monitor is located on spill pipe.No DWF.Monor response to storm events.Sensor cleaned thoroughly from ragging. Data downloaded. |  |  | Spill pipe - data looks ok. |  |  | FM located on spill pipe.Data looks ok.Sensor cleaned from ragging. |  |  | FM located on spill pipe.Data looks ok. Good scatter |  |  | Removal Requested 19/09 |  |  | Removed
FM70 |  | Poor data.Velocity drops down to zero during DWF.Responsive to rainfall. Reinstalled into Pipe B |  |  | High velocities and very low depth (some negative). Poor velocity data until 13/08/24 but better after that. However, depth data is negative from 13/08/24 so no flows have been calculated. | Query with Enviromontel |  | Poor data (high velocity, low depth). No suitable alternative. |  |  | Poor data.High velocity and low depths.Data drops out at mutliple times. |  |  | Poor data, velocity, flow and depth drop outs and depth below 0. Some evidence of diurnal profile and storm reponse. Relacted to pipe x. |  |  | FM was relocated to X pipe on 10/09. Good data, flow follows storm events and has small DWF |  |  | See FM160
FM71 |  | Good data. Evidence of diurnal profile. Good storm response. |  |  | Good data.Evidence of diurnal profile.Good storm response.Scattergraph looks reasonable.Sensor cleaned thoroughly from ragging. |  |  | Good data. |  |  | Data looks good.Responsive to storm events.Diurnal profile is evident.Data drops out from 04/09/2024. |  |  | Good data, diurnal profile and storm response evident. Step up in data around 20th Aug. |  |  | Good data, no data after midday 16/09 |  |  | Data looks good.No data after 24/09/2024 |  |  | Good data. Makes sense with u/s FM160 | Leave in for winter flows (Catchment FM) |  | Good data. |  |  | Good data. |  |  | Good data.
FM72 |  | Located on bifurcation. No flow in DWF. Minimal flow in storm events. |  |  | Located on bifurcation.Responsive to rainfall.No flow in DWF.Sensor cleaned from ragging. |  |  | Bifurcation. Flows recorded duirng heavy rainfall. |  |  | FM located at bifurcation.Storm responsive to heavy storms.No flow in DWF. |  |  | No data since 3rd Sept | Query with Enviromontel |  | Flow does not respond to light rainfall (FM located on dry pipe/bifurcation) |  |  | FM located on bifurcation.No response to light rainfall. |  |  | Site visit required - unit does not dial in through the internet | Leave in for winter flows (Catchment FM) |  | Bifurcation - response to rainfall |  |  | Bifurcation - minor response to rainfall. |  |  | Bifurcation - minor response to rainfall. | Remove
FM73 |  | Good data.Responsive to storm events.Scattergraph looks reasonable.Sensor cleaned thoroughly from ragging |  |  | Good data.Responsive to storm events.diurnal profile is evident.Scattergraph looks reasonable.Sensor cleaned from ragging. |  |  | Velocities dropped out towards end of interim - needs cleaning. |  |  | Data looks good.Responsive to storm events.Velocity drop out at the end of flow survey period(from 04/09/2024). |  |  | Data ok. Level seems to change- sensor in wrong place? Notes suggest offset. | Query with Enviromontel |  | Good depth data. Velocities drop out from 12/09., clear response to storm events but no dwf |  |  | Good data |  |  | Telemetry data downloaded. Velocity drop outs. | Report to Enviromontel |  | Good depth data, continued velocity drop outs. Assess during next interim. |  |  | Good depth data. Velcocities improved after last clean. Dropped out again on 14/10, but sensor has been cleaned again. |  |  | Poor velocity data. sensor has been cleaned.
FM74 |  | Telemetry download. Located on bifurcation. Very low flows during DWF. Some rainfall response. |  |  | Telemetry data downloaded.FM is located on bifurcation.Responsive to only one storm event. |  |  | Unable to access. Data looks ok considering low flows. |  |  | FM located at bifurcation.Low flows.Data looks ok. |  |  | FM on bifurcation. Negative depths. Responsive to storm events. |  |  | FM on bifurcation, no flow. Ok data for depth and velocity |  |  | FM located on bifurcation.Negative depth values. |  |  | Unable to access. Parked cars blocking room for setup | To be removed |  | Unable to access due to parked cars | To be removed |  | Data downloaded. Monitor removed
FM75 |  | Data looks ok. Slow flow.Wide scatter.Diurnal profile is evident.Responsive to rainfall.Sensor cleaned thoroughly from ragging |  |  | Data looks good.Slow flow.Scattergraph looks reasonable.diurnal profile is evident.Responsive to rainfall.Sensor cleaned from ragging. |  |  | Unable to access. |  |  | Data looks good.Slow flow.Responsive to storm events.Diurnal profile is evident.Scattergraph looks good.Velocity drops out from 04/09/2024. |  |  | No data since 3rd Sept | Query with Enviromontel |  | Good data, small flow and depth readings, velocity follows a diurnal pattern |  |  | Good data.Low flow and velocitiy values.Evidence of diurnal pattern. |  |  | Monitor removed. | Removed
FM76 |  | Data looks ok. Steady flow.Diurnal profile is evident.Responsive to rainfall.Sensor cleaned thoroughly from ragging |  |  | Telemetry data downloaded.Data looks good.diurnal profile is evident.Responsive to rainfall.Scattergraph looks good. |  |  | Good data. |  |  | Good data |  |  | Data looks good.diurnal profile is evident.Responsive to rainfall.Scattergraph looks good. |  |  | Ok data, little/no flow or depth data. Velocities look good. |  |  | Okay |  |  | Monitor removed. | Removed
FM77 |  | Data looks good.Scattergraph looks good.diurnal profile is visible.Responsive to storm events.Sensor cleaned from ragging |  |  | Data looks ok.Sacttergraph looks good.diurnal profile is visible.Responsive to storm events.ensor removed, cleaned thoroughly from ragging and refitted. |  |  | Good data. |  |  | Good data.Responsive to storm events and evidence of diurnal profile.Data drops out from 04/09/2024 |  |  | Good data.Responsive to storm events and evidence of diurnal profile. Good scatter |  |  | Good data. |  |  | Okay |  |  | Good data. | Retain - Cwmbrwla x3 CSOs BIF |  | Good data. |  |  | Good data. |  |  | Good data.
FM78 |  | Telemetry download - 4 days available. Minimal flow in DWF. Storm response evident. Located on outgoing pipe. |  |  | Responses to rainfall but some negative depth values |  |  | Data ok considering low flows. |  |  | Responsive to rainfall events.Some negative depth values. |  |  | Responsive to rainfall events.Some negative depth values. Good scatter |  |  | Removal Requested 19/09 |  |  | Removed
FM80 |  | Telemetry download - 4 days available. Reasonable data.Wide scatter.diurnal profile is visible.Responsive to rainfall. |  |  | Some velocity drift but generally okay |  |  | Good data. |  |  | Good data. |  |  | Diurnal profile and storm response evident. Good data, good scatter. Possible step/drift in data around 23rd Aug |  |  | Removal Requested 19/09 |  |  | Removed
FM81 |  | No velocity data and depth data in first couple of days. Good data following this. |  |  | Okay |  |  | Good data. |  |  | Good data.Velocity drops out after 04/09/2024. |  |  | Diurnal profile and storm response evident. Good scatter |  |  | Removal Requested 19/09 |  |  | Removed
FM82 |  | No velocity data in the first couple of days. Good data following this. |  |  | Okay |  |  | Good data. |  |  | Good data |  |  | Diurnal profile and storm response evident. Posisble data drop out and surcharge? No data since 8th Sept | Query with Environmental |  | Good depth data, diurnal profile. Velocities dropped out from 07/09. |  |  | Data looks ok.Few velocity drop out. |  |  | Telemetry data downloaded. To be removed. | To be removed. |  | Removed
FM83 |  | Evidence of pumping station downstream.But none in asset plan or model. | Check with contractor about location of pumping station nearby. |  | Okay. Velocity/depth no longer as irregular Steady flow, surchagred so sensor could not be cleaned |  |  | Data ok, evidence of significant surcharge. |  |  | Data looks ok.Evidence of surcharge. |  |  | Ok data, storm response evident. Evidence of surcharge |  |  | Good data, small response to storm event. Evidence of surcharge. |  |  | Okay |  |  | Good data. | Retain - Cwmbrwla x3 CSOs |  | No data this interim from 30/09 | Query with Environmentel |  | Velocities dropped out from 30/09 to 08/10. Data ok after this. |  |  | Good data
FM84 |  | Evidence of pumping station downstream.But none in asset plan or model. | Check with contractor about location of pumping station nearby. |  | Okay. Velocity/depth no longer as irregular Steady flow, surchagred so sensor could not be cleaned Few velocity drops but nothing major |  |  | Good data. |  |  | Good data.Velocity drop out after 04/09/2024. |  |  | Ok data and scatter, storm response and dirunal profile mostly evident. |  |  | Good data, responds to storm event and has dwf. Velocity shows diurnal profile. |  |  | Okay |  |  | Good data. | Retain - Cwmbrwla x3 CSOs |  | Good data. |  |  | Good data. Evidence of slow response. |  |  | Good data. Surcharged, so unable to enter. Data downloaded
FM85 |  | DWF looks ok. Depth showing negative value during storm events. | Query with Enviromontel |  | Data looks ok, some negative depth values. |  |  | Data ok, minimal storm response. |  |  | Poor data.Negative depth values.Minor storm response.Velocity drops out. | Query with Enviromontel |  | Evidence of diurnal profile and storm response. Some negative depth values. Scatter ok. Drift in velocity data? |  |  | Good data, responds to storm event, no negative depths after 15/09, velocity shows clear diurnal profile |  |  | Dta looks good.Evidence of dirurnal profile. |  |  | Reasonable data. | Retain - Cwmbrwla x3 CSOs |  | Reasonable data. |  |  | Depths too low for accurate reading but no alternatives. Key site. |  |  | Depths too low for accurate reading but no alternatives. Key site.
FM86 |  | No flow in DWF. Large storm response, but doesn't line up with rainfall - delayed by >1hr. | Query with Enviromontel |  | No flow in DWF. Bifurcation US to FM85 which shows DWF, possible flow goes to FM85 in dry conditions. Peak flows still don't line up with rainfall. | Query with Enviromontel |  | Data still delayed when compared to rainfall. | Query with Enviromontel |  | Low flow in DWF.Delayed storm response.No data recorded after 05/09/2024. |  |  | Data ok, storm response evident but low flows in DWF. |  |  | Ok data, responds to storm event however no/ minimal dwf because depths drop below 0. Velocity follows diurnal profile |  |  | Okay |  |  | Good data. | Retain - Cwmbrwla x3 CSOs |  | Good data. |  |  | Data seems ok. High velocities. |  |  | Data seems ok. High velocities.
FM87 |  | Poor data.Velocity drops down to zero. Slow flow and ragging. Alt:U/S and D/S of MH0604 | Relocate |  | As per interim 1 |  |  | Poor data. | Relocate to spill pipe? |  | Poor data - depth only site due to no alternatives (unable to relocate to spill pipe due to screen) |  |  | Very low flows, storm response evident. |  |  | Very low depths. Depth readings improve from 11/09 but velocities become more patchy. Sensor cleaned from ragging. No flow data since 11/09, negative depth reading throughout. Velocity follows storm event. |  |  | Very low flow.Velocity data drops out multiple times. |  |  | Doesn't make sense with u/s FMs 85 and 86 | Retain - Cwmbrwla x3 CSOs |  | Potential volume imbalance to u/s FMs 85 and 86 - ragged and flow is shallow, no alternatives. | Query with Environmentel |  | Poor data - low velocities and depths. No alternativies. Key site. |  |  | Improved data
FM88 |  | Evidence of pumping station upstream.But none in asset plan or model. | Check with contractor location of pumping station nearby |  | Veloctiy data sporadic but improvement from interim 1 |  |  | Good data |  |  | Data looks ok..Velocity values looks uneven. | Query with Enviromontel |  | Okay. responds to rainfall, velocity drops during storms Slow flow, sensor heavily ragged and greased - see photos, cleaned |  |  | Good data, velocity is high. Flows responds to storm event and follows diurnal profile. |  |  | Okay |  |  | Good data. | Retain - Cwmbrwla x3 CSOs |  | Good data, surcharge evident. |  |  | Good data, surcharge evident. |  |  | Good data, surcharge evident. Fast flow.
FM90 |  | Telemetry download - Very low flows - small u/s catchment. Minor storm response. |  |  | Data not retrieved. |  |  | Low flows - small u/s catchment. Data ok. |  |  | Site visit required |  |  | Negative depth recordings and low dwf. Flow has small response to rainfall Trickle flow |  |  | Poor flow data and very varied, sometimes negative depth readings. No clear response to storm event, no dwf. Small u/s catchment - ok. |  |  | Poor flow data.Some negative depth values |  |  | Ok data, low flows. 1 good storm captured since installation of d/s FM161. | Leave in for one more storm. |  | Continued low flows - no additional storms during interim 9 - leave in for additional week / storm. |  |  | Low flows. A few good storms now recorded with relocated FM161 so monitors around Glanowen CSO can be removed. | Remove
FM91 |  | Telemetry download. diurnal profile visible. Scattergraph looks reasonable.No data recorded after 8/8/2024 |  |  | Okay |  |  | Data ok. |  |  | Data looks ok.Negative depth values and there is gap in velocity data. | Query with Enviromontel |  | Okay. Negative depth on 6+5/09. Low/no dwf |  |  | Ok data, velocity seems to roughly follow diurnal profile. little/no dwf and varied depth readings. |  |  | Negative depth data.No clear response to storm. |  |  | Ok data, low flows. 1 good storm captured since installation of d/s FM161. | Leave in for one more storm. |  | Continued low flows, data okay - minor additional storm during interim 9 - leave in for additional week / storm. |  |  | Low flows. | Remove
FM92 |  | No DWF recorded. Storm response. | Review in interim 2 |  | No DWF recorded. Storm response. Trickle flow. US FM91 has DWF, Bifurcation US to FM93 but no data for this FM | Query with Enviromontel |  | Bifurcation. Data ok. |  |  | Data looks ok. |  |  | Okay. Negative depth recorded on 7/09. Low/no dwf. Enviromontel: Relocated to C pipe as requested. |  |  | FM relocated to C pipe on 12/09. Improved data. |  |  | See FM161
FM93 |  | Telemetry download. No data except small storm response in first storm event. | Review in interim 2 |  | No velocity data for either interim. Possible that this is the secondary leg of the bifurcation upstream, hence no flows. |  |  | Bifurcation. Minor response to 1 rainfall event across survey period. |  |  | FM located on bifurcation.Minor storm response. |  |  | FM on bifurication. No flow. Depth and velocity respond to rainfall |  |  | No velocity or flow data since 7/09 as FM on bifurcation therefore no dwf, or response to small storm event. |  |  | FM located on bifurcation.No flow. |  |  | High level bifurcation. Minor spill recorded. 1 good storm captured since installation of d/s FM161. | Leave in for one more storm. |  | High level bifurcation - no more storms recorded in Interim 9. |  |  | Bifurcation - no flows recorded. | Remove
FM94 |  | No data recorded in the first 4 days.Good data after this. |  |  | Okay |  |  | Good data |  |  | Good data. |  |  | good data |  |  | Good data. Flows follow diurnal profile, flow responds to small storm event. |  |  | Data looks good.Evidence of diurnal profile |  |  | Good data. | Leave in for winter flows (Catchment FM) |  | Good data. |  |  | Good data. |  |  | Good data.
FM95 |  | Pumped flow. data looks good. |  |  | Okay |  |  | Good data. |  |  | Pumped flow.Data looks good. |  |  | Good data. Few minor velocity drops |  |  | Pumped flow, good data. |  |  | Pumped flow.Good data |  |  | Good data. | Leave in for winter flows (Catchment FM) |  | Good data. |  |  | Good data. |  |  | Good data.
FM96 |  | Telemetry download. Low depths and minimal velocities recorded. FM located in bifurcation. | TBC |  | No DWF, step change in depth data, weak response to storms. Trickle flow, sensor heavily ragged - deep cleaned Numerous bifurcations US Wide scatter | Query with Enviromontel |  | Poor data. | Relocate? |  | Poor data | FM to be Removed |  | Responds to rainfall, low flow during dry periods. Velocity data sporadic | Removal Planned |  | Removal Requested 19/09 |  |  | Removed
FM97 |  | Telemetry download. Minimal velocities recorded. Surcharged depths in second storm event. |  |  | Velocity data only present between 15/08 - 20/08 - drifts towards end of this period. Slow flow, sensor cleaned from ragging Takes several housing estates and buisnesses Wide scatter. | Query with Enviromontel |  | Poor data. | Relocate? |  | Poor data - depth only site | Query with Enviromontel |  | No velocity data after 7/09 Slow flow, cleaned from ragging |  |  | Velocity returns after 9/09, good data, velocity and flow responds to storm events, small dwf |  |  | Okay |  |  | Good depth data, velocities dropped out. | Leave in for winter flows (Catchment FM) |  | Good depth data, velocities dropped out. |  |  | Good depth data, velocity drop outs. Evidence of surcharge. |  |  | Good depth data, velocity drop outs. Sensor cleaned | Remove
FM98 |  | Telemetry download. Data looks good.diurnal profile is evident.Flow responsive to rainfall.Scattergraph looks reasonable.No data recoded after 8/8/2024 |  |  | No velocity data for interim 2 | Review in interim 3 once cleaned? |  | Poor data | Enviromontel to clean |  | Poor data | Query with Enviromontel |  | good data, no dwf Slow flow, sensor cleaned from ragging and silt. Sensor is offset. |  |  | Depth data ok. Velocities affected by ragging/grease. |  |  | Okay.No DWF |  |  | Good depth data. Poor velocity data. | Leave in for winter flows (Catchment FM) |  | Good depth data. Poor velocity data. |  |  | Good depth data. Poor velocity data. |  |  | Good depth data. Poor velocity data.
FM99 |  | Telemetry download. Minor DWF diurnal profile. Storm response. |  |  | Okay |  |  | Good data |  |  | Data looks good. |  |  | Good data, but little-no flow in dry weather |  |  | Data looks reasonable. |  |  | Good data.Data drops out on 18/09/2024 |  |  | OK data. Very low DWF. | Leave in for winter flows (Catchment FM) |  | OK data. Very low DWF. |  |  | OK data. Very low DWF. |  |  | Good data. Low flows.
FM100 |  | Poor data up to 08/08/24, ok after this. Velocity drop out during second storm. Diurnal profile and storm response evident. |  |  | Okay |  |  | Good data. Evidence of surcharge. |  |  | Good data .Evidence of surcharge. |  |  | Good data, evidence of diurnal flow and storm response. Evidence of surcharge |  |  | Good data, evidence of diurnal flow and storm response. Evidence of surcharge. Unable to check as car parked on top of manhole |  |  | Good data |  |  | Good data. | Leave in for winter flows (TEN) |  | Good velocity data, depth data show drift throughout interim. | Query with Enviromontel |  | Good data. Evidence of surcharge during storms. |  |  | Good data. Evidence of surcharge during storms.
FM103 |  | Telemetry downloaded. No velocities recorded in DWF. Storm response. Wide scatter. | Review in interim 2 |  | No velocities recorded in DWF. Storm response. Standing water. Sensor cleaned from silt Wide scatter. |  |  | No velocities recorded in DWF. Storm response. Sensor Clear Wide scatter. | Relocate? |  | No velocities recorded in DWF. Storm response. Sensor Cleaned Wide scatter. No alternatives, on trunk, leave in for depth readings | Relocate? |  | No velocities recorded in DWF Sensor cleaned |  |  | No velocity despite depths during DWF. Sensor cleaned. Storm response |  |  | Removed
FM104 |  | Okay |  |  | Okay |  |  | Okay |  |  | Okay |  |  | Okay |  |  | Diurnal profile evident, storm response, good data |  |  | Removed
FM105 |  | Okay |  |  | Okay |  |  | Okay |  |  | Okay |  |  | Okay |  |  | Diurnal profile evident, storm response, good data. Some negative depths |  |  | Removed
FM106 |  | Okay |  |  | Okay |  |  | Okay |  |  | Okay |  |  | Okay |  |  | Recent data has drifted readings. Sensor cleaned and recalibrated. |  |  | Drop in velocity but okay. Steady flow. Sensor cleaned from ragging and grease. |  |  | Monitor removed. | Removed
FM107 |  | Okay, few velocity sags but not major. |  |  | Okay |  |  | Okay |  |  | Okay |  |  | Okay |  |  | Recent data may have drift and unusual storm response for location. Sensor cleaned |  |  | Okay |  |  | Good data. | Leave in for winter flows (TEN) |  | Good data. |  |  | Good data. (Volume balance with u/s FM147 but this monitor has now been removed). |  |  | Good data.
FM108 |  | Velocity data spikey throughout period, no DWF. Covers bifurcation, so DWF may go other route? Wide scatter. | Review in interim 2 |  | As per interim 1 | Query with Enviromontel |  | poor velocity data due to slow flow | Relocate? |  | poor velocity data due to slow flow. Storm Response. Environmontel response: poor site with very low flows Sensor Cleaned. Leave in for depth readings. | relocate? |  | Poor velocity data.Steady flow, sensor cleaned from ragging and grease. | Query with Environmental |  | Data ok, storm response evident and some diurnal profile. Recalibration and clean |  |  | Okay |  |  | Good data. | Leave in for winter flows (TEN) |  | Good data. |  |  | Good data. |  |  | Good data.
FM110 |  | Okay |  |  | Okay |  |  | Okay |  |  | Okay |  |  | Okay |  |  | Good data, storm and diurnal response evident. |  |  | Okay |  |  | Depth data unreliable (signficant increase from u/s FM111. | Raise with Enviromontel |  | Continued high depths - unreliable, significant increase from u/s FM111 | Query with Enviromontel |  | Continued volume imbalance (signficant increase from FM111 to FM110). | Check with Enviromontel |  | Poor site | Remove.
FM111 |  | Okay |  |  | Okay |  |  | Okay |  |  | Okay |  |  | Okay.Gap in data on 29/08/2024 |  |  | Good data, storm and diurnal response evident. |  |  | Okay |  |  | Good data. | Leave in for winter flows (TEN) |  | Good data. |  |  | Continued volume imbalance (signficant increase from FM111 to FM110). | Check with Enviromontel |  | Good data.
FM112 |  | Okay |  |  | Depth data looks unreliable. | Query with Enviromontel |  | As per interim 2. Enviromontel response: manual depth checks required | Previous Query |  | Being relocated | relocate |  | To be relocated |  |  | Depth data drift from beginning of readings. Monitor relocated on 16/09 (FM162 - awaiting data). |  |  | See FM162
FM114 |  | Okay |  |  | Okay |  |  | Okay |  |  | Okay |  |  | Okay |  |  | Good data, storm and diurnal response evident. |  |  | Okay |  |  | Good data. | Leave in for winter flows (TEN) |  | Good data. |  |  | Good data. |  |  | Data ok.
FM115 |  | Velocity issues at beginning of interim, impoved after first few days, however flows much less than expected - large upstream catchment. Records pumped flow from upstream. Scatter okay. | Relocate? |  | Unable to lift manhole cover |  |  | Data looks okay but would expect more flow? | Query with Enviromontel |  | Data looks okay but would expect more flow, FM114 Vol (DS monitor) = 78,000, FM115 = 10,000 | Query with Enviromontel |  | Data looks ok.Volume imbalance issues. FM 114 Vol (DS monitor)=2,00,000, FM115=32,000 | Query with Environmental |  | Good data, storm and diurnal response evident. Volume imbalance remains |  |  | Okay. Volume imbalance remains Steady flow. Sensor cleaned from ragging and grease. Sensor calibrated to match manual measurements. |  |  | Good data | Leave in for winter flows (TEN) |  | Good data |  |  | Velocity looks a bit patchy towards end of interim, but sensor has now been cleaned. |  |  | Jump in velocities | Query with Enviromontel
FM116 |  | Velcities look strange. Review in next interim. |  |  | Few velocity sags but generally okay, responds to rainfall. Wide scatter |  |  | Okay |  |  | Okay |  |  | Okay |  |  | Significant data drift/issue with readings. Sensor had moved due to turbulant flow, monitor removed. | Query with environmentel |  | Awaiting relocation (FM165) |  |  | Awaiting relocation (FM165)
FM117 |  | Okay |  |  | Okay |  |  | Data drops out from 24/08 onwards | Query with Enviromontel |  | Okay |  |  | Okay |  |  | Depth and flow data drop out and velocity data drift. Sensor dislodged in pipe and refitted on site visit. |  |  | Awaiting relocation (FM166) |  |  | Awaiting relocation (FM166) |  |  | Awaiting relocation (FM166)
FM118 |  | Good depth data. Velocity issues throughout, flows down to zero in DWF. On main trunk. Wide scatter. Alt: 3no. MHs DS, 2no MHs US misses small lateral but minor flow. | Relocate? |  | As per interim 1. Slow flow, snesor cleaned from ragging. No suitable alternatives |  |  | Data drops out from 19/08 onwards | Query with Enviromontel |  | Velocity drops outs few times towards end of interim sensor cleaned Wide scatter. Weekly cleaning - leave in for depth only. | Query with Enviromontel |  | Velocity drops out at multiple times.Sensor removed cleaned and refitted offset | Query with Environmental |  | Velocity and flow data drop outs. Depth data ok but appears to drift. Cleaned from raggin on visit. |  |  | Velocity drops out, depth okay, responds to rainfall |  |  | Good depth data, poor velocity data. | Leave in for winter flows (TEN) |  | Good depth data, poor velocity data. |  |  | Good depth data, poor velocity data. |  |  | Good depth data, poor velocity data.
FM119 |  | Okay |  |  | Good data |  |  | Okay |  |  | Okay |  |  | Data looks good. |  |  | Good data, storm and diurnal response evident. Removal requested 19/09, nothing in site notes. |  |  | Removed
FM120 |  | Okay |  |  | Good data |  |  | Okay |  |  | Okay |  |  | Okay |  |  | Good data, storm and diurnal response evident. Removal requested 19/09, nothing in site notes. |  |  | Removed
FM121 |  | Telemetry download No depth or velocity data after first couple of days. Take several hosuing estate so should be sizable flow. Scatter okay. | Review in interim 2 |  | Slow flow and ragging results in fairly poor data. Wide scatter. |  |  | As per interim 2. | Query with Enviromontel |  | Velocity looks okay but low flows, would expect more. Wide Scatter | Query with Enviromontel |  | Low flows.Wide scatter |  |  | Very low depths (some negative). Low flow. |  |  | Very low flows in dry weather, data looks okay during storms |  |  | Data ok. low depths. | Leave in for winter flows (TEN) |  | Data ok. low depths. |  |  | Data ok. low depths. |  |  | Good data
FM122 |  | Okay |  |  | Good data. |  |  | Site visit required - unit does not dial in through the internet | Site Visit |  | Site visit required - unit does not dial in through the internet | Site Visit |  | Poor data.Negative depth values. |  |  | Good data, storm and diurnal response evident. Removal requested 19/09, nothing in site notes. |  |  | Okay
FM123 |  | Okay, possibly some veloctiy drift present. Duirnal pattern presnt but small. Only takes few housing estate so expect small DWF. Scatter okay. |  |  | Ok considering small u/s catchment and low flows. |  |  | Site visit required - unit does not dial in through the internet | Site Visit |  | Site visit required - unit does not dial in through the internet | Site Visit |  | Data downloaded.Data looks ok. |  |  | Good data, storm and diurnal response evident. Removal requested 19/09, nothing in site notes. |  |  | Removed
FM124 |  | Okay |  |  | Good data. |  |  | Okay |  |  | Okay |  |  | Okay |  |  | Data changed on 06/09 - negative deptsh recorded adn velocities reduced. No flows recorded. | Query with Environmental |  | No Flows recorded Moniotr swapped - sensor refitted. |  |  | Data not provided. | Leave in for winter flows (TEN) |  | No data since 27/09 | Query with Enviromontel |  | Poor data. Monitor swapped. |  |  | Good data.
FM125 |  | Data not retrieved. | Site Visit |  | No depths recorded | Query with Enviromontel |  | Data drops out from 24/08 onwards Environmontel reposnse to interim 2: Incorrect depth units - sensor heavily ragged | Previous Query |  | No velocity data Environmontel response: Sensor cleared from ragging and come off ring during last week site visit. Visited 04/09 and data looks better. | Review Interim 5 |  | Poor data.Huge gaps in velocity data. | Query with Environmental |  | Poor data. Further flow and velocity data drop outs and large sections of negative depths | Query with Environmental |  | Poor data. Further flow and velocity data drop outs and negative depths |  |  | Poor data. | Query with Enviromontel |  | Poor data, velocities dropping out and consistent negative depth data throughout interim. | Query with Enviromontel |  | Poor data through most of interim. Some storm response. |  |  | Poor data. Unable to access - parked car. | Remove
FM126 |  | Okay |  |  | Relatively small u/s catchment, so low DWF. Good storm response. |  |  | Okay |  |  | Okay |  |  | to be relocated |  |  | Potential data issue - depth, flow and velocity trends do not match previous. Monitor relocated. |  |  | See FM163
FM127 |  | Telemetry download. Velocity issues throughout. US of FM128 - vol balance issue. Wide scatter. Alt: Numerous MHs US and DS e.g. 6010, 6012 | Relocate? |  | Very poor data (steep pipe) | Relocate |  | As per interim 2. No response from Environmontel in query sheet | Previous Query |  | Vol balance issue, being relocated as of 26/08? | Query with Enviromontel |  | to be relocated |  |  | Good data. |  |  | See FM164
FM128 |  | Okay |  |  | Data ok. |  |  | Okay |  |  | Okay |  |  | Good data |  |  | Reasonable data. |  |  | Okay |  |  | Good data. | Leave in for winter flows (USCO) |  | Good data. |  |  | Good data. |  |  | Good data. | Remove
FM129 |  | Telemetry download. No DWF at night. High spikey flows during day. Only takes few buidlings, trade? Wide scatter. |  |  | Depth ok, velocities spiky. Very small u/s catchment so ok. |  |  | As per interim 2. Okay |  |  | Site visit required - unit does not dial in through the internet | Site Visit |  | Poor data | Query with Environmental |  | Small catchment - low flows. Ok. |  |  | Small catchment - low flows. Ok. |  |  | Ok data. Low flow in DWF. Some ragging | Leave in for winter flows (USCO) |  | Ok data. Low flow in DWF. Some ragging |  |  | Ok data. Low flow in DWF. Some ragging |  |  | Ok data. Low flow in DWF. Some ragging. Sensor cleaned. | Remove
FM130 |  | Telemetry download. No flows recorded during DWF. Storm response evident. DS of FM129, vol balance issue. Wide scatter. |  |  | Depth ok, no velocity in DWF. Very small u/s catchment so ok. |  |  | As per interim 2. Okay |  |  | Site visit required - unit does not dial in through the internet | Site Visit |  | Sensor cleaned - data downloaded.No flows recorded in DWF. |  |  | Very poor velocity data. Only depth data is usable. Sensor cleaned from grease. |  |  | Very poor velocity data. Only depth data is usable. Slow flow. Sensor cleaned from ragging. |  |  | Ok data. Low flow in DWF. Some ragging | Leave in for winter flows (USCO) |  | Ok data. Low flow in DWF. Some ragging |  |  | Ok data. Low flow in DWF. Some ragging |  |  | Poor data - very low flows | Remove
FM131 |  | Telemetry download. Depth data ok but no velocity data. Alt: DS MH 5202 incoming or US MHs but misses small lateral line | Relocate? |  | No velcoities recorded. No alternatives. Leave in for depths. |  |  | As per interim 2. Okay Environmontel reponse: Silty slow flow, can try offset |  |  | Poor data, no velocity for most of interim Environmontel Response: Large amount of silt upstream which silts up when cleaning. To be visited to offset. | Review Interim 5 |  | Poor data .No velocity recorded in most of the period. | Query with Environmental |  | Very poor velocity data. Only depth data is usable. Sensor cleaned from ragging and silt. Sensor offset to avoid further silt. |  |  | Very poor velocity data. Only depth data is usable. Slow flow. Sensor cleaned from ragging. |  |  | Very poor data due to silt. Sensor adjusted - check next interim. | Leave in for winter flows (TEN) |  | Removal requested
FM132 |  | Telemetry download. Low flows in DWF. Storm response recorded | Review in interim 2 |  | Reasonable data. |  |  | Okay |  |  | Okay |  |  | Data looks good. |  |  | Good data. |  |  | Okay |  |  | Good data. | Leave in for winter flows (TEN) |  | Good data. |  |  | Good data. |  |  | Good data.
FM133 |  | Okay, veloctiy data spikey throughout period. Wide scatter. |  |  | Data ok. |  |  | Okay |  |  | Okay |  |  | Okay |  |  | No data since 13/09. Data ok up to this point. |  |  | Okay. Spikes in velocity |  |  | Good data. | Leave in for winter flows (TEN) |  | Good data. |  |  | Good data. |  |  | Good data.
FM134 |  | Okay, veloctiy data spikey throughout period. Wide scatter. |  |  | Random spikes in velocity (up ot 6m/s) which don't correspond to rainfall | Query with Enviromontel |  | As per interim 2. No response from Environmontel in query sheet | Previous Query |  | Random spikes in velocity Environmontel Response: Investigating | Being Investigated |  | Spikes in velocity data | Query with Environmental |  | No data since 05/09 | Query with Environmental |  | Site visit required - unit does not dial in through the internet |  |  | Good data. | Leave in for winter flows (TEN) |  | Good data. |  |  | Good data. |  |  | Good data.
FM135 |  | No flow data for entire interim except during storm. Installed on high level bifurcation |  |  | No spills recorded. |  |  | Okay. No flow data for entire interim except during storm. Installed on high level bifurcation |  |  | Okay. No flow data for entire interim except during storm. Installed on high level bifurcation Dry pipe |  |  | FM located on high level bifurcation.No flow data exept storm events. |  |  | FM located on high level bifurcation.No flow recorded. |  |  | FM located on high level bifurcation.No flow recorded. |  |  | FM located on high level bifurcation. Spills recorded. | Leave in for winter flows (TEN) |  | FM located on high level bifurcation - no spill recorded during interim. |  |  | Bifurcation. No spills recorded. |  |  | Bifurcation. No spills recorded.
FM136 |  | No flow data for entire interim. Alt: only 1no. MH US 8091 with 2no. Incoming pipes so needs to be outgoing. | Relocate? |  | Very poor data | Relocate? |  | As per interim 2. Environmontel reponse: Silty slow flow, can try offset | Previous Query |  | As per previous interims. Environmontel reponse: No alts, to be removd | Remove |  | Poor data. | Query with Environmental |  | Removal Requested 19/09 |  |  | Removed
FM137 |  | Veloctiy data only during rainfall periods. Takes flow from housing estate only so would expect much DWF. Wide scatter. | Review in interim 2 |  | Good depth data. No velcoity data in DWF. Some storm response | Query with Enviromental |  | As per interim 2. Environmontel reponse: Silty slow flow, can try offset | Previous Query |  | As per previous interims. Environmontel reponse: No alts, to be removd | Remove |  | No flow in DWF. |  |  | Removal Requested 19/09 |  |  | Removed
FM138 |  |  |  |  | Data looks ok, diurnal profile and storm response both evident. |  |  | Okay |  |  | Okay |  |  | Okay |  |  | Okay |  |  | Okay |  |  | Good data. | Leave in for winter flows (TEN) |  | Good data. |  |  | Good data. |  |  | Good data.
FM139 |  |  |  |  | Data looks ok considering small u/s catchment. Scatter ok. |  |  | Okay |  |  | Okay |  |  | Okay |  |  | Okay |  |  | Okay |  |  | Good data. | Leave in for winter flows (TEN) |  | Good data. |  |  | Very low depths. Good velocities. |  |  | Good data.
FM140 |  | Flows much lower than expected. | Relocate? |  | Data ok. |  |  | Okay |  |  | Okay |  |  | Data looks ok.No data from 03/09/2024 | Query with Environmental |  | Removal Requested 19/09 |  |  | Removed
FM141 |  | Negative depths |  |  | Negative depths |  |  | Negative depths |  |  | As per previous interims. Environmontel reponse: No alts, to be removd | Remove |  | Negative depths | Query with Environmental |  | Removal Requested 19/09 |  |  | Removed
FM142 |  | Velocity data drops out several times. FM141 is okay DS. Scatter okay. | Review in interim 2 |  | Velocity issue due to ragging. Small u/s catchment and unlikely to be suitable alternative. |  |  | As per interim 2. Environmontel reponse: Silty slow flow, can try offset | Previous Query |  | As per previous interims. Environmontel reponse: No alts, to be removd | Remove |  | Negative depth data.Data improved from 30/08/2024 | Query with Environmental |  | Okay |  |  | Removed
FM143 |  | Negative depth data. Foul pipe. Alt: Numerous DS MHs e.g. 1802, 1813 | Relocate? |  | Depth data improved from 15/08. However, depths still reduce during rainfall. | Query with Enviromontel |  | Depth data still suspect No response from Environmontel in query sheet | Previous Query |  | Some Depth data still suspect No response from Environmontel in query sheet. FM to be removed. | Previous Query |  | Negative depth data. | Query with Environmental |  | Removal Requested 19/09 |  |  | Removed
FM144 |  | Okay, velocity drops out couple times but no major issues. Foul pipe. |  |  | Data looks ok. |  |  | Okay |  |  | Okay |  |  | Okay |  |  | Okay |  |  | Okay
FM145 |  | Okay. Storm pipe |  |  | Storm pipe - good response. |  |  | Data drops out from 24/08 onwards when rainfall recorded Much less vol than DS FM146 | Query with Enviromontel |  | As per previous interims. Environmontel reponse: No alts, to be removd | Remove |  | FM located on storm pipe.Data drops out multiple times.Negative depth values. | Query with Environmental |  | Removal Requested 19/09 |  |  | Removed
FM146 |  | Data not retrieved. | Site Visit |  | Storm pipe, d/s of FM145. Good response. |  |  | Okay |  |  | Okay |  |  | Okay |  |  | Good data. |  |  | Okay | [5 empty] | Removed
FM147 |  | Data not retrieved. | Site Visit |  | Good data |  |  | Okay |  |  | Okay |  |  | Okay |  |  | Good data. |  |  | Site visit required - unit does not dial in through the internet
FM148 |  | Data not retrieved. | Site Visit |  | Storm pipe. Significant volume imbalance with u/s FM60. | Query with Enviromontel |  | As per interim 2. No response from Environmontel in query sheet | Previous Query |  | As per previous interims. Environmontel reponse: to be removd | Remove |  | As per previous interims. |  |  | Removal Requested 19/09 |  |  | Removed
FM149 |  | Okay, velocity and depth drop out at one point Flows small in DWF? |  |  | Data looks ok. Reasonable scatter. |  |  | Okay |  |  | Okay |  |  | Okay |  |  | Good data. Velocities drop out towards end of period. Needs cleaning | Query with Environmental |  | Velocity drops out for most of interim, back toward end |  |  | Good data. | Leave in for winter flows (Catchment FM) |  | Good data. |  |  | Data ok but depths are low. |  |  | Depth data looks suspect. Sensor cleaned from ragging and grease.
FM150 |  | Velocity issues throughout, no DWF Alt: 2no. MHs US. 4107 use incoming or outgoing. 4101 only use outgoing. | Relocate? |  | Poor data - low flows. | Query with Enviromontel |  | As per interim 2. Environmontel reponse: Sensor deep cleaned 22/08 - see site sheet photos | Previous Query |  | As per previous interims. Environmontel reponse: to be removd | Remove |  | Poor data-low flows |  |  | Removal Requested 19/09 |  |  | Removed
FM151 |  | N/A |  |  | Good data |  |  | Site visit required - unit does not dial in through the internet | Site Visit |  | Okay |  |  | Okay |  |  | Good data |  |  | Okay |  |  | Good data. | Retain - Cwmbrwla x3 CSOs |  | Good data. |  |  | Good data. |  |  | Good data.
FM152 |  | N/A |  |  | Good data |  |  | Okay |  |  | Okay |  |  | Negative depth values | Query with Environmental |  | Good data |  |  | Okay |  |  | Good data. | Retain - Cwmbrwla x3 CSOs |  | Good data. |  |  | Good data. |  |  | Good data.
FM153 |  | N/A |  |  | N/A |  |  | N/A - Installed |  |  | Data okay, velocities drop out during low flows |  |  | Poor data.Negative depth values. | Query with Environmental |  | Good data. Velocities drop out towards end of period but sensor has been cleaned of ragging. |  |  | Okay, low flow |  |  | Good data. | Retain - Cwmbrwla x3 CSOs |  | Good data. |  |  | Good data. |  |  | Good data.
FM154 |  | N/A |  |  | N/A |  |  | N/A - Installed |  |  | Okay |  |  | Okay |  |  | Good data. |  |  | Okay |  |  | Good data. | Retain - Cwmbrwla x3 CSOs |  | Good data. |  |  | Good data. |  |  | Good data.
FM155 |  | FM not installed |  |  | FM not installed |  |  | FM not installed |  |  | FM not installed |  |  | FM not installed |  |  | Installed 20/09 - relocation of FM06 |  |  | Okay |  |  | Good data. Makes sense with u/s FM04. | Leave in for winter flows (linked to SOIMP) |  | Good data. |  |  | Good data. |  |  | Good data.
FM156 |  | FM not installed |  |  | FM not installed |  |  | FM not installed |  |  | FM not installed |  |  | FM not installed |  |  | Installed 03/09 - relocation of FM32 |  |  | Okay. Spikes in velocity Steady flow. Sensor cleaned from ragging. |  |  | Good data. | Remove |  | Awaiting removal.
FM157 |  | FM not installed |  |  | FM not installed |  |  | FM not installed |  |  | FM not installed |  |  | FM not installed |  |  | Installed 19/09 - relocation of FM34 |  |  | No Data |  |  | Good data. | Leave in for one more storm. |  | Good data. |  |  | Good data. |  |  | Good data. | Remove
FM158 |  | FM not installed |  |  | FM not installed |  |  | FM not installed |  |  | FM not installed |  |  | FM not installed |  |  | Installed 10/09 - relocation of FM35 |  |  | Okay, couple minor velocity drops |  |  | Awaiting data. | Leave in for one more storm. |  | Awaiting data - none since 25/09. FM being left in to capture one more storm. | Query with Environmental |  | No data. | Query with Enviromontel |  | Reasonable data. | Remove
FM159 |  | FM not installed |  |  | FM not installed |  |  | FM not installed |  |  | FM not installed |  |  | FM not installed |  |  | Installed 10/09 - relocation of FM67 |  |  | Okay | [5 empty] | Removed
FM160 |  | FM not installed |  |  | FM not installed |  |  | FM not installed |  |  | FM not installed |  |  | FM not installed |  |  | Installed 10/09 - relocation of FM70. Good data. |  |  | Okay |  |  | Good data. Makes sense with d/s FM71 |  |  | Awaiting removal.
FM161 |  | FM not installed |  |  | FM not installed |  |  | FM not installed |  |  | FM not installed |  |  | FM not installed |  |  | Installed 12/09 - relocation of FM92 |  |  | Okay. Negative Depths |  |  | Good data. One good storm recorded. | Leave in for one more storm. |  | Good data. No data after 03/10 so unable to tell if storm recorded on 06/10, leave FM in. |  |  | Good data. | Remove
FM162 |  | FM not installed |  |  | FM not installed |  |  | FM not installed |  |  | FM not installed |  |  | FM not installed |  |  | Installed 16/09 - relocation of FM112 |  |  | Flow drops out for most of interim |  |  | Very poor depth data. Remove. | Remove |  | Awaiting removal.
FM163 |  | FM not installed |  |  | FM not installed |  |  | FM not installed |  |  | FM not installed |  |  | FM not installed |  |  | Installed 18/09 - relocation of FM126 |  |  | Installed on spill pipe. Reacts to rainfall. |  |  | Spill pipe. Records spill. | Leave in for winter flows (USCO) |  | Spill pipe, no spills recorded this interim. |  |  | Spill pipe, no spills recorded this interim. |  |  | Spill pipe, no spills recorded this interim.
FM164 |  | FM not installed |  |  | FM not installed |  |  | FM not installed |  |  | FM not installed |  |  | FM not installed |  |  | Installed 05/09 - relocation of FM127 |  |  | Okay, minor velocity drops |  |  | Ok data. | Leave in for winter flows (USCO) |  | No data this interim. | Query with Environmental |  | Good data. |  |  | Good data. | Remove
FM165 | [28 empty] | Good data. |  |  | Good data.
FM166 | [28 empty] | Good data. |  |  | Good data.
DM01 |  | No data retrieved |  |  | Data Ok |  |  | Data OK |  |  | Data OK |  |  | Data OK |  |  | Dry weather - some depths recorded but likely to be erroneous data | [5 empty] | Telemetry data downloaded |  |  | No data this interim. | Query with Environmental |  | Good data. |  |  | Good data
DM02 |  | No data retrieved |  |  | No data retrieved |  |  | No data since 27/08 |  |  | No data since 27/08 - site visit planned for 9th Sept |  |  | Data OK |  |  | No data since 09/09 | [5 empty] | Site visit required - unit does not dial in through the internet |  |  | Removed
DM03 |  | No data retrieved |  |  | Depths drop out during storm events. |  |  | Some data drop out - pump operation levels changed or DM issue |  |  | Data drop out and erratic - pump operation levels changed or DM issue | Query with Enviromontel |  |  |  |  | Monitor was swapped on 09/09 but still experiencing data drop outs during storm events. | [5 empty] | Site visit required - unit does not dial in through the internet |  |  | Removed
PL01 |  | No data retrieved |  |  | No data retrieved | [20 empty] | Removed
PL02 |  | No data retrieved |  |  | No data retrieved | [11 empty] | Removal Requested 19/09 | [8 empty] | Removed
PL03 |  | No data retrieved |  |  | No data retrieved | [20 empty] | Awaiting removal.
PL04 |  | No data retrieved |  |  | No data retrieved
PL05 |  | No data retrieved |  |  | No data retrieved
PL06 |  | No data retrieved |  |  | No data retrieved
PL07 |  | No data retrieved |  |  | No data retrieved | [20 empty] | Removed
PL08 |  | No data retrieved |  |  | No data retrieved | [20 empty] | Removed
PL09 |  | No data retrieved |  |  | No data retrieved | [20 empty] | Removed
RG01 |  | Data file empty - needs investigating |  |  | RG swapped - workshop to download data off old unit |  |  | No data received | Query with Environmental |  | No data received | Query with Environmental |  | RG SWAPPED | [8 empty] | OK |  |  | OK |  |  | OK
RG02 |  | Rain Gauge visited, filter cleaned. All ok |  |  | ok |  |  | OK |  |  | OK |  |  | Okay | [8 empty] | OK |  |  | OK |  |  | OK
RG03 |  | Rain Gauge visited, filter cleaned. Unable to connect for test. Confirmed RG is calling in online Data look suspect compared to other RGs |  |  | Rainfall values much smaller than other monitors | Query with Environmental |  | Rainfall values much smaller than other monitors | Query with Environmental |  | Rainfall values much smaller than other monitors | Query with Environmental |  | RG relocated - see sheet for details. | [8 empty] | Last storm (29/09) not picked up by RG03 |  |  | Storm (06/10) not picked up by RG03. | Query with Environmental |  | Rain Gauge swapped
RG04 |  | All okay - data downloaded |  |  | ok |  |  | OK |  |  | OK |  |  | Okay | [8 empty] | OK |  |  | OK |  |  | OK
RG05 |  | Unable to gain access. Locked gate |  |  | ok |  |  | OK |  |  | OK |  |  | RG SWAPPED | [8 empty] | Faulty data. |  |  | Faulty data. | Query with Environmental |  | OK
RG06 |  | Data file empty - needs investigating |  |  | Couldn't get comms. Swapped RG. |  |  | No data received | Query with Environmental |  | No data received | Query with Environmental |  | RG SWAPPED | [8 empty] | OK |  |  | OK |  |  | OK
RG07 |  | Rain Gauge visited, filter cleaned. All ok |  |  | ok |  |  | OK |  |  | OK |  |  | Okay | [8 empty] | OK |  |  | OK |  |  | OK
RG08 |  | Rain Gauge visited, filter cleaned. All ok |  |  | ok |  |  | OK |  |  | OK |  |  | Okay | [8 empty] | OK |  |  | OK |  |  | OK
RG09 |  | Rain Gauge visited, filter cleaned. All ok |  |  | ok |  |  | OK |  |  | OK |  |  | Okay | [8 empty] | OK |  |  | OK |  |  | OK
RG10 |  | Installed - no data for interim 1 |  |  | Rainfall values much smaller than other monitors | Query with Environmental |  | OK |  |  | OK |  |  | Okay | [8 empty] | OK |  |  | OK |  |  | OK
RG11 |  | No comms. Confirmed RG is offline. RG to be changed at next visit |  |  | RG swapped - workshop to download data off old unit |  |  | No data - RG failure? | Query with Environmental |  | OK |  |  | Okay | [8 empty] | OK |  |  | OK |  |  | OK
RG12 |  | Installed - no data for interim 1 |  |  | Awaiting data file |  |  | OK |  |  | OK |  |  | Okay | [8 empty] | OK |  |  | OK |  |  | OK
RG13 |  | All okay - data downloaded |  |  | ok |  |  | OK |  |  | OK |  |  | Okay | [8 empty] | OK |  |  | OK |  |  | OK
RG14 |  | All okay - data downloaded |  |  | ok |  |  | OK |  |  | OK |  |  | Okay | [8 empty] | OK |  |  | OK |  |  | OK
RG15 |  | All okay - data downloaded |  |  | ok |  |  | OK |  |  | OK |  |  | Okay | [8 empty] | OK |  |  | OK |  |  | OK
RG16 |  | All okay - data downloaded |  |  | ok |  |  | OK |  |  | OK |  |  | RG checked - All okay | [8 empty] | OK |  |  | OK |  |  | OK

## DRY DAYS (hidden)
Note - this tab has been moved to a new calculation in the 'verification' Folder of Model Build

## Storm selection
Storm Events
To ensure that the rainfall storms meet the WaPUG criteria ensure that the Rainfall Assessment_V2 spreadsheet is completed.

## Storm compliance
Storm Events
To ensure project success check that each monitor recorded satisfactory data during each storm event. This sheet allows an audit trail into the reasons why the flow survey was removed. If sufficient data was not recorded then why was the flow survey removed?
2no. Events
| 23/08/2024 - 25/08/2024 | 2024-09-01 | 2024-09-06
FM / DM / PL | Storm A | Storm B | Storm C | Storm D | COMMENT | Storm Coverage (Not exclusive to events state to the left)
| COMMENT | COMMENT | COMMENT | COMMENT
FM01 | Y - | Y - | N - No Data |  |  | 3+
FM02 | Y - | Y - | Y - |  |  | 3+
FM03 | Y - | N - No Data | N - No Data |  |  | 3+
FM04 | Y - | Y - | N - No Data |  |  | 3+
FM05 | Only data for 1no. Event | N - Poor Data | N - No Data |  | Secondary leg of bifurcation, few small responses to storms | 3+
FM06 | Y - | Y - | N - No Data |  | Very small flow, responds to rainfall | 3+
FM09 | Y - | Y - Velocity drops out briefly | N - No Data |  |  | 3+
FM10 | Y - | Y - Velocity drops out briefly | N - No Data |  |  | 3+
FM11 | Y - | Y - | N - No Data |  | DS bifurcation, likely high level pipe | 3+
FM13 | Y - | Y - | N - No Data |  | Low flows, small US catchment. No readings beyond 22nd August | 3+
FM14 | Y - depth only | N - No Data | Y - depth only |  | Depth only response to storm | 3+
FM15 | N - No Data | N - No Data | N - No Data |  |  | 3+
FM16 | Y - | Y - | Y - Negative depth data? |  |  | 3+
FM17 | Y - | Y - but zero flow data prior to rain | N - No Data |  |  | 3+
FM18 | N - No Data | N - No Data | N - No Data |  | Spill Pipe | 2
FM19 | Y - | Y - | Y - |  |  | 3+
FM20 | Y - | Y - | N - No Data |  | Spill Pipe | 3+
FM21 | Y - | Y - | Y - |  |  | 3+
FM22 | Y - | Y - | N - No Data |  |  | 3+
FM23 | Y - | N - Poor Data | N - No Data |  |  | 3+
FM24 | Y - | Y - | N - No Data |  |  | 3+
FM25 | Y - | Y - | N - No Data |  |  | 3+
FM26 | Y - | Y - | N - No Data |  |  | 3+
FM27 | Y - | Y - | N - No Data |  |  | 3+
FM28 | Y - | Y - | N - No Data |  |  | 3+
FM29 | Y - | Y - Negative depth data? | Y - Small Storm Response |  |  | 3+
FM30 | Y - | Y - | Y - |  |  | 3+
FM31 | Y - | Y - | N - No Data |  |  | 3+
FM32 | Y - | Y - Negative depth data? | N - No Data |  |  | 3+
FM33 | Y - | Y - | N - No Data |  |  | 3+
FM34 | Y - Negative depth data? | Y - Negative depth data? | Y - |  |  | 3+
FM35 | Y - | Y - | N - No Data |  |  | 3+
FM37 | N - No Storm Response | N - No Storm Response | Y - |  | Only repsonse to 1no. Storm in entire period up to interim 4 | 1
FM38 | Y - Small Storm Response | Y - | N - No Data |  |  | 3+
FM39 | Y - | N - No Data | N - No Data |  | Limited data after 29/08 | 3+
FM40 | Y - | Y - | N - No Data |  |  | 3+
FM41 | Y - | Y - | N - No Data |  |  | 3+
FM42 | Y - | Y - | Y - |  |  | 3+
FM43 | N - Poor Data | N - No Data | N - No Data |  | poor data, velocty drop out for most of survey | 1
FM44 | Y - | Y - | Y - |  |  | 3+
FM45 | Y - | Y - | Y - Drop in velocity during storms |  |  | 3+
FM47 | N - No Data | N - Poor Data | N - No Flow |  | poor data, velocty drop out for most of survey | 1
FM48 | Y - | Y - | Y - |  |  | 3+
FM49 | Y - | Y - | N - No Data |  |  | 3+
FM50 | N - No Data | N - No Data | N - No Data |  | No readings beyond 20th August | 3+
FM51 | Y - | Y - | Y - |  |  | 3+
FM54 | Y - | N - | Y - |  | Spill Pipe | 3+
FM55 | Y - | Y - | N - No Data |  | Very small flow, responds to rainfall | 3+
FM56 | Y - | Y - | N - No Data |  |  | 3+
FM57 | Y - | Y - | N - No Data |  |  | 3+
FM58 | N - No Data | N - bad quality data | N - No Data |  | No Flow data for entire survey | 0
FM59 | Y - | Y - | Y - |  |  | 3+
FM60 | Y - | N - No Data | N - No Data |  | No readings beyond 28th August | 3+
FM61 | Y - | Y - | Y - |  | Low flows, adequate velocities, poor depth data | 3+
FM62 | N - No Data | N - No flow | N - No Data |  | No Flow data for entire survey | 0
FM63 | Y - | Y - | N - No Data |  |  | 3+
FM64 | Y - | Y - | N - No Data |  |  | 3+
FM65 | Y - | Y - | N - No Data |  |  | 3+
FM66 | Y - Negative depth data? | Y - | N - No Data |  |  | 3+
FM67 | Y - | Y - | N - No Data |  |  | 3+
FM68 | Y - | Y - | Y - |  |  | 3+
FM69 | Y - | Y - | N - No Data |  |  | 3+
FM70 | Y - Velocity drops out for 1no. Event | Y - | N - No Data |  |  | 3+
FM71 | Y - | Y - | N - No Data |  |  | 3+
FM72 | Y - | Y - | N - No Data |  |  | 3+
FM73 | Y - | Y - | N - No Data |  |  | 3+
FM74 | Y - Negative depth data? | Y - | Y - Negative depths and very low flow |  |  | 3+
FM75 | Y - | Y - | N - No Data |  |  | 3+
FM76 | Y - | Y - | Y - |  |  | 3+
FM77 | Y - | Y - | N - No Data |  |  | 3+
FM78 | Y - Negative depth data? | Y - | Y - |  |  | 3+
FM80 | Y - | Y - | Y - |  |  | 3+
FM81 | Y - | Y - | N - No Data |  |  | 3+
FM82 | Y - | Y - | Y - |  |  | 3+
FM83 | Y - | N - velocity drops out | Y - |  |  | 3+
FM84 | Y - | Y - | N - No Data |  |  | 3+
FM85 | Y - Small storm response and negative depths | Y - Small storm response and negative depths | N - No Data |  |  | 3+
FM86 | Y - | Y - | N - No Data |  |  | 3+
FM87 | Y - Small storm response | Y - Small storm response | N - No Data |  |  | 3+
FM88 | Y - | Y - | N - No Data |  |  | 3+
FM90 | Y - low depths | Y - low depths | Y - low depths |  | Very low depths and velocities | 3+
FM91 | Y - Negative depth data? | Y - | Y - |  |  | 3+
FM92 | N - No Data | N - No Data | Y - |  | No data until 5th September | 2
FM93 | N - Poor Data | N - No Data | Y - Small storm response |  | Possible secondary leg of bifurcation | 3+
FM94 | Y - | Y - | Y - |  |  | 3+
FM95 | Y - | N - Poor Data | Y - |  |  | 3+
FM96 | Y - | Y - | N - No Data |  |  | 3+
FM97 | N - Poor Data | N - Poor Data | Y - Poor Data |  | Slow flow, velocity regularly drops out | 3+
FM98 | N - No Data | N - Poor Data | N - No Data |  | Large periods with no data | 1
FM99 | Y - | Y - | Y - |  |  | 3+
FM100 | Y - Veloctiy drops out for 1no. Event | Y - Veloctiy drops out | Y - |  |  | 3+
FM103 | Y - | Y - | N - No Data |  | Standing water, no DWF velocity | 3+
FM104 | Y - | Y - | N - No Data |  |  | 3+
FM105 | Y - Negative depth data? | Y - Negative depth data? | N - No Data |  |  | 3+
FM106 | Y - | Y - | N - No Data |  |  | 3+
FM107 | Y - breif Velocity drops during storms | Y - velocity drops few times | N - No Data |  |  | 3+
FM108 | Y - | Y - | N - No Data |  |  | 3+
FM110 | Y - | Y - | Y - |  |  | 3+
FM111 | Y - | Y - | Y - |  |  | 3+
FM112 | Y - | Y - | Y - |  |  | 3+
FM114 | Y - | Y - breif drop in velocity | N - No Data |  |  | 3+
FM115 | Y - | Y - | N - No Data |  |  | 3+
FM116 | Y - | Y - | Y - Negative depth data? |  |  | 3+
FM117 | Y - | Y - | N - No Data |  |  | 3+
FM118 | Y - | Y - | N - No Data |  |  | 3+
FM119 | Y - | Y - | N - No Data |  |  | 3+
FM120 | Y - | Y - | N - No Data |  |  | 3+
FM121 | Y - | Y - | Y - |  |  | 3+
FM122 | Y - | Y - | Y - |  |  | 2
FM123 | Y - | Y - | Y - |  |  | 2
FM124 | Y - | Y - | Y - |  |  | 3+
FM125 | N - No Data | N - No Data | N - No Data |  | Large periods with no data | 0
FM126 | Y - Negative depth data? | Y - | Y - |  |  | 3+
FM127 | N - Poor Data | Y - | N - No Data |  |  | 1
FM128 | Y - | N - velocity drops out | Y - |  |  | 3+
FM129 | Y - | N - No Data | N - No Data |  | No readings beyond 29th August. Velocity issues during storms | 2
FM130 | Y - | N - No Data | N - No Data |  | No readings beyond 29th August. Small US catchment | 3+
FM131 | N - Poor Data | N - Poor Data | N - No Data |  | Silt US, slow flow | 0
FM132 | Y - Negative depth data? | Y - Negative depth data? | Y - |  |  | 3+
FM133 | Y - Negative depth data? | Y - Negative depth data? | N - No Data |  |  | 3+
FM134 | Y - Negative depth data? | Y - Negative depth data? | N - No Data |  |  | 3+
FM135 | Y - | N | N - No Data |  | high level bifurcation | 3+
FM136 | N - Poor Data | N - Poor Data | N - No Data |  | Silty slow flows | 0
FM137 | N - Poor Data | N - Poor Data | N - No Data |  | Silty slow flows | 0
FM138 | Y - | Y - | Y - |  |  | 3+
FM139 | Y - | Y - | N - No Data |  |  | 3+
FM140 | Y - | Y - | N - No Data |  |  | 3+
FM141 | N - Poor Data | N - Poor Data | N - No Data |  | Issues with depth
FM142 | Y - Negative depth data? | Y - | N - No Data |  |  | 3+
FM143 | N - Poor Data | Y - Negative depth data? | N - No Data |  |  | 3
FM144 | Y - | Y - | N - No Data |  |  | 3+
FM145 | Y - Veloctiy drops out for 1no. Storm and negative depths | N - Poor Data | N - No Data |  | Large periods with no data | 3
FM146 | Y - | Y - | N - No Data |  |  | 3+
FM147 | Y - | Y - | N - No Data |  |  | 3+
FM148 | Y - Negative depth data? | Y - Negative depth data? | Y - |  |  | 3+
FM149 | Y - | Y - | N - No Data |  |  | 3+
FM150 | Y - Sporadic Veloctiy but some storm response | Y - Sporadic Veloctiy but some storm response | N - No Data |  |  | 3+
FM151 | Y - | Y - but high velocities when no rain | Y - |  |  | 3+
FM152 | Y - | Y - | Y - |  |  | 3+
FM153 | N/A | N/A | N/A |  |  | 0
FM154 | N/A | N/A | N/A |  |  | 0
FM155
FM156
FM157
FM158
FM159
FM160
FM161
FM162
FM163
FM164
DM01
DM02
DM03
PL01
PL02
PL03
PL04
PL05
PL06
PL07
PL08
PL09

## Removals & Relocations
Monitor | CSO | Scheme | Verification Level | Deliverable | Reason | Storm COMMENT | Storm COVERAGE | Dry Day COMMENT | Dry Day COVERAGE | Data Quality | Comment | Decision | BB check/comments | Slow response | Data Quality | Remove? | Summary | No.
FM01 | Storm Overflow at Heol Eithrim - 72682 | SOWQAS P2 | 3 | IDP1 | Asset Incoming Flow | 0 | 3+ | 0 | 0 | Good storm coverage, poor data during DWF - low flows. | Okay for removal - low flows | Removal / Removed |  |  |  |  | Removal / Removed | 108
FM02 | Storm Overflow at Heol Eithrim - 72682 | SOWQAS P2 | 3 | IDP1 | Asset Continuation Flow | 0 | 3+ | 0 | 2+ | Good storm & DWF coverage - good data | Okay for removal - good data | Removal / Removed |  |  |  |  | Retain - linked to SO IMP1 asset d/s | 6
FM03 | Heol Y Nant/Sybil Street Clydach CSO - 70975 | SOWQAS P2 | 3 | IDP1 | Asset Incoming Flow | 0 | 3+ | Very Low Flow in DWF | 1 | Storm coverage, poor data during DWF - low flows | IDP2 asset d/s, hydraulically linked to SO IMP1 - to be retained | Retain - linked to SO IMP1 asset d/s |  | Low | Poor / low | Yes | Retain - SO IMP1 | 4
FM04 | Heol Y Nant/Sybil Street Clydach CSO - 70975 | SOWQAS P2 | 3 | IDP1 | Asset Incoming Flow | 0 | 3+ | 0 | 2+ | Good storm & DWF coverage - good data | IDP2 asset d/s, hydraulically linked to SO IMP1 - to be retained | Retain - linked to SO IMP1 asset d/s |  | Low | Good | No | Retain - SO IMP1 Bifurcation | 1
FM05 | Heol Y Nant/Sybil Street Clydach CSO - 70975 | SOWQAS P2 | 3 | IDP1 | Asset Incoming Flow | Secondary leg of bifurcation, few small responses to storms | 3+ | No DWF-bifurcation | 0 | Secondary leg of bifurcation - no DWF or storm response | IDP2 asset d/s, hydraulically linked to SO IMP1 - to be retained | Retain - linked to SO IMP1 asset d/s |  | Low | Poor / low | Yes | Retain - Catchment FM | 13
FM06 | Heol Y Nant/Sybil Street Clydach CSO - 70975 | SOWQAS P2 | 3 | IDP1 | Asset Continuation Flow | Very small flow, responds to rainfall | 3+ | 0 | 1 | Storm coverage, poor data during DWF - low flows | Relocated 20/09 to FM155 - removed | Removal / Removed |  |  |  |  | Retain - more Data | 0
FM09 | Inco CSO Clydach Swansea - 72001 | SO IMP1 (AMP8) | 4 | IDP2 | Asset Incoming Flow | 0 | 3+ | 0 | 1 | Storm coverage, limited DWF due to data | FM around IDP2 asset, SO IMP1 - to be retained | Retain - SO IMP1 |  | Medium | Good | Possible | Retain - Cwmbrwla x3 CSOs BIF | 2
FM10 | Inco CSO Clydach Swansea - 72001 | SO IMP1 (AMP8) | 4 | IDP2 | Asset Continuation Flow | 0 | 3+ | 0 | 2 | Good storm & DWF coverage - good data | FM around IDP2 asset, SO IMP1 - to be retained | Retain - SO IMP1 |  | Medium | Good | Possible | Retain - Cwmbrwla x3 CSOs | 10
FM11 | Bifurcations at SN69011203 & SN69011208 | - | 4 | - | Lev 4 Bifurcation | DS bifurcation, likely high level pipe | 3+ | No DWF-high level bifurcation | 0 | Good storm, no DWF as on BIF - good data during storms | FM at BIF u/s of IDP2 asset, SO IMP1 - to be retained | Retain - SO IMP1 Bifurcation |  | Low | Good | Possible | Retain - TEN | 18
FM13 | Canal CSO Towpath Off Hebron Road, Clydach - 72004 | SO IMP1 (AMP8) | 4 | IDP2 | Asset Continuation Flow | Low flows, small US catchment. No readings beyond 22nd August | 3+ | 0 | 0 | Storm coverage, depth only for DWF | FM around IDP2 asset, SO IMP1 - to be retained | Retain - SO IMP1 |  | Low | Poor / low | Yes | Retain - TEN Bifurcation | 3
FM14 | Canal CSO Towpath Off Hebron Road, Clydach - 72004 | SO IMP1 (AMP8) | 4 | IDP2 | Asset Incoming Flow | Depth only response to storm | 3+ | No DWF-Small upstream catchment | 0 | Depth only response to storm, no DWF - low flows | FM around IDP2 asset, SO IMP1 - to be retained | Retain - SO IMP1 |  | Low | Poor / low | Yes | Retain - UCSO high spiller | 0
FM15 | CSO at Quarry Road Clydach (Point 125) - 73381 | SOWQAS P2 | 3 | IDP1 | Asset Continuation Flow | 0 | 3+ | 0 | 0 | Good depth, erratic velocity | IDP2 asset d/s, hydraulically linked to SO IMP1 - to be retained | Retain - linked to SO IMP1 asset d/s |  | Low | Poor / low | Yes | TOTAL | 165
FM16 | CSO at Quarry Road Clydach (Point 125) - 73381 | SOWQAS P2 | 3 | IDP1 | Asset Incoming Flow | 0 | 3+ | 0 | 2+ | Good storm & DWF coverage - decent data | IDP2 asset d/s, hydraulically linked to SO IMP1 - to be retained | Retain - linked to SO IMP1 asset d/s |  | Low | Poor / low | Yes | FMs to REMAIN | 57
FM17 | Ynys Y Mond Rd CSO, Glais - 52472 | UCSO | 4 | IDP2 | Asset Incoming Flow | 0 | 3+ | 0 | 0 | Depth only, poor velocity data | Poor data, UCSO driver (low spiller) - to be removed | Removal / Removed
FM18 | Ynys Y Mond Rd CSO, Glais - 52472 | UCSO | 4 | IDP2 | Asset Continuation Flow | Spill Pipe | 2 | No DWF-located on spill pipe | 0 | Spill pipe - storms picked up | Spill pipe - storm flows. UCSO driver (low spiller) - to be removed | Removal / Removed
FM19 | CSO Ynystawe (Point 86 New Ma) - 52490 | SOAF (Live) (High Spills 60+ and Lower 8 Dilution) | 3 | None | Asset Incoming Flow | 0 | 3+ | Small upstream catchment | 0 | Good storm & DWF coverage - good data | Okay for removal - good data | Removal / Removed
FM20 | CSO Ynystawe (Point 86 New Ma) - 52490 | SOAF (Live) (High Spills 60+ and Lower 8 Dilution) | 3 | None | Asset Continuation Flow | Spill Pipe | 3+ | 0 | 0 | Data during spills - spill pipe | Okay for removal | Removal / Removed
FM21 | CSO Ynysforgan Roundabout - 73413 | SOWQAS P2 | 3 | IDP1 | Asset Incoming Flow | 0 | 3+ | 0 | 2+ | Good storm & DWF coverage - good data | Okay for removal - good data | Removal / Removed | No need to have both FM21 and FM22, FM21 has better data so retained
FM22 | CSO Ynysforgan Roundabout - 73413 | SOWQAS P2 | 3 | IDP1 | Asset Continuation Flow | 0 | 3+ | 0 | 0 | Some velocities, generally depth only | Depth only - okay for removal, retain FM21 u/s | Removal / Removed
FM23 | Bifurcation at SS67996304 | - | 3 | - | Lev 3 Bifurcation | 0 | 3+ | 0 | 2 | Good depth, erratic velocity | Retain for catchment FM - north (Clydach) | Retain - Catchment FM |  | Medium | Average | Possible
FM24 | Heol Dulais CSO at Birchgrove - 51193 | SOWQAS P2 | 3 | IDP1 | Asset Incoming Flow | 0 | 3+ | Small upstream catchment | 2 | Storm and DWF coverage - low flows | Okay for removal - low flows | Removal / Removed
FM25 | Heol Dulais CSO at Birchgrove - 51193 | SOWQAS P2 | 3 | IDP1 | Asset Incoming Flow | 0 | 3+ | 0 | 1 | Storm and DWF coverage - low flows | Okay for removal - low flows | Removal / Removed
FM26 | Heol Dulais CSO at Birchgrove - 51193 | SOWQAS P2 | 3 | IDP1 | Asset Continuation Flow | 0 | 3+ | 0 | 2 | Good storm & DWF coverage - good data | Okay for removal | Removal / Removed
FM27 | Glais CSO / Glais SPS - 50944 | SOWQAS P2 | 3 | IDP1 | Asset Incoming Flow | 0 | 3+ | 0 | 2+ | Good storm & DWF coverage - good data | IDP2 asset u/s, UCSO (low spiller) - to be removed | Removal / Removed
FM28 | Felin Fran CSO Walters Rd Llansamle - 71292 | SOWQAS P2 | 3 | IDP1 | Asset Incoming Flow | 0 | 3+ | 0 | 2 | Good storm & DWF coverage - good data | Okay for removal - retain FM29 d/s | Removal / Removed | No need to have both FM28 and FM29, FM29 has better data so retained
FM29 | Felin Fran CSO Walters Rd Llansamle - 71292 | SOWQAS P2 | 3 | IDP1 | Asset Continuation Flow | 0 | 3+ | 0 | 2+ | Good storm & DWF coverage - good data | Retain for catchment FM - flows entering Fendrod SPS (FM50 d/s poor data) | Retain - Catchment FM |  | Medium | Good | No
FM30 | Glais CSO / Glais SPS - 50944 | SOWQAS P2 | 3 | IDP1 | Asset Incoming Flow | 0 | 3+ | 0 | 1 | Good storm, limited DWF coverage - low flows | Low flows, IDP2 asset u/s, UCSO (low spiller) - to be removed | Removal / Removed
FM31 | No6 Heol Dyfan CSO, Morriston - 70961 | UCSO | 4 | IDP2 | Asset Incoming Flow | 0 | 3+ | Small u/s catchment | 0 | Good storm, limited DWF coverage - low flows | Hydraulically linked to FM156 which is to be retained to gain more data | Removal / Removed
FM32 | No6 Heol Dyfan CSO, Morriston - 70961 | UCSO | 4 | IDP2 | Asset Incoming Flow | 0 | 3+ | 0 | 0 | Poor data - low flows | Relocated to X 03/09 to FM156 - removed | Removal / Removed
FM33 | No6 Heol Dyfan CSO, Morriston - 70961 | UCSO | 4 | IDP2 | Asset Continuation Flow | 0 | 3+ | No DWF-located on spill pipe | 0 | Spill pipe - storms picked up | Hydraulically linked to FM156 which is to be retained to gain more data | Removal / Removed
FM34 | CSO 80 Pentrpoeth Rd Morriston - 70959 | SOWQAS P2 | 3 | IDP1 | Asset Incoming Flow | 0 | 3+ | 0 | 0 | Good velocity, erratic depth - storms okay | Relocated 19/09 to FM157 - removed | Removal / Removed | Relocated to Treharne Road?
FM35 | CSO 80 Pentrpoeth Rd Morriston - 70959 | SOWQAS P2 | 3 | IDP1 | Asset Incoming Flow | 0 | 3+ | 0 | 2 | Good velocity, erratic depth - storms okay | Relocated to X 10/09 to FM158 - removed | Removal / Removed
FM37 | CSO Halfway Crymlyn Road PS - 50961 | SOWQAS P2 | 3 | IDP1 | Asset Incoming Flow | Only repsonse to 1no. Storm in entire period up to interim 4 | 1 | 0 | 2+ | Poor data throughout | Okay for removal - poor data | Removal / Removed
FM38 | Trallwyn Community Centre CSO - 52484 | SOWQAS P2 | 3 | IDP1 | Asset Incoming Flow | 0 | 3+ | 0 | 2 | Good storm & DWF coverage - good data | Okay for removal | Removal / Removed
FM39 | Adj 27 Bethel Rd Llansamlet CSO - 71453 | SOWQAS P2 | 3 | IDP1 | Asset Incoming Flow | Limited data after 29/08 | 3+ | 0 | 1 | Limited data after 29/08 - okay coverage | Okay for removal | Removal / Removed
FM40 | Adj 27 Bethel Rd Llansamlet CSO - 71453 | SOWQAS P2 | 3 | IDP1 | Asset Continuation Flow | 0 | 3+ | 0 | 2 | Good storm & DWF coverage - good data | Okay for removal | Removal / Removed
FM41 | Trallwyn Community Centre CSO - 52484 | SOWQAS P2 | 3 | IDP1 | Asset Continuation Flow | 0 | 3+ | 0 | 2 | Good storm & DWF coverage - good data | Okay for removal | Removal / Removed
FM42 | Peniel Green Road CSO - 52461 | SOWQAS P2 | 3 | IDP1 | Asset Incoming Flow | 0 | 3+ | 0 | 0 | Good storm & DWF coverage - good data | Okay for removal | Removal / Removed
FM43 | Peniel Green Road CSO - 52461 | SOWQAS P2 | 3 | IDP1 | Asset Continuation Flow | poor data, velocty drop out for most of survey | 1 | 0 | 0 | Poor data throughout | Okay for removal - poor data | Removal / Removed | Potential to relocate? No continuation flows on CSO 52461 otherwise - only L3, remove
FM44 | Samlet Rd CSO 103 - 71419 | SOAF (Live) | 3 | None | Asset Incoming Flow | 0 | 3+ | 0 | 2 | Good storm & DWF coverage - good data | Okay for removal - retain FM45 d/s | Removal / Removed | No need to have both FM44 and FM45, FM45 has better data so retained
FM45 | Samlet Rd CSO 103 - 71419 | SOAF (Live) | 3 | None | Asset Continuation Flow | 0 | 3+ | 0 | 2+ | Good storm & DWF coverage - good data | Retain for catchment FM - flows entering Fendrod SPS (FM50 d/s poor data) | Retain - Catchment FM |  | High | Medium | Possible
FM47 | CSO 73 Crown St Morriston Swansea - 72289 | SOWQAS P2 | 3 | IDP1 | Asset Continuation Flow | poor data, velocty drop out for most of survey | 1 | 0 | 0 | Depth only response to storm | Okay for removal - depth only | Removal / Removed
FM48 | Westbury St CSO Swansea - 72399 | UCSO | 4 | IDP2 | Asset Incoming Flow | 0 | 3+ | 0 | 1 | Depth only, poor velocity data | Poor data, UCSO driver (low spiller) - to be removed | Removal / Removed | On level 4 asset - to be retained
FM49 | Bifurcation at SS67970505 | - | 3 | - | Lev 3 Bifurcation | 0 | 3+ | 0 | 2 | Good storm & DWF coverage - good data | Retain for catchment FM - bifurcation u/s of Fendrod SPS | Retain - Catchment FM |  | Medium | Good | Possible
FM50 | Catchment Split - Fendrod SPS - 70010 | - | - | - | Asset Incoming Flow | No readings beyond 20th August | 3+ | 0 | 0 | No data beyond 20/08 - need data | Okay for removal - u/s catchment monitored by u/s FMs | Removal / Removed | Keep in u/s monitors instead which cover most of catchment - can be removed
FM51 | Wychtree Street CSO Morriston - 72401 | SOWQAS P1 | 3 | IDP1 | Asset Incoming Flow | 0 | 3+ | 0 | 1 | Good storm & DWF coverage - good data | Retain for catchment FM - flows entering Fendrod SPS (FM50 d/s poor data) | Retain - Catchment FM |  | Medium | Medium | Possible
FM54 | Westbury St CSO Swansea - 72399 | UCSO | - | IDP2 | Asset Continuation Flow | Spill Pipe | 3+ | No DWF-located on spill pipe | 0 | Spill pipe - low flows | Spill pipe - low flows, UCSO driver (low spiller) - to be removed | Removal / Removed | On level 4 asset - to be retained
FM55 | Mynyddgarnllwyd CSO Swansea - 72480 | SOWQAS P2 | 3 | IDP1 | Asset Incoming Flow | Very small flow, responds to rainfall | 3+ | 0 | 2 | Poor data - very low flows | Okay for removal - very low flows | Removal / Removed
FM56 | Mynyddgarnllwyd CSO Swansea - 72480 | SOWQAS P2 | 3 | IDP1 | Asset Incoming Flow | 0 | 3+ | 0 | 2 | Adequate data - low flows | Okay for removal - low flows | Removal / Removed
FM57 | Mynyddgarnllwyd CSO Swansea - 72480 | SOWQAS P2 | 3 | IDP1 | Asset Continuation Flow | 0 | 3+ | 0 | 2 | Good storm & DWF coverage - some velocity data drop-out | Okay for removal | Removal / Removed
FM58 | Bifurcation at SS65962901 | - | 3 | - | Lev 3 Bifurcation | No Flow data for entire survey | 0 | No DWF-bifurcation | 0 | Poor data - BIF, no flows | Okay for removal - poor data so not to be used as catchment FM | Removal / Removed
FM59 | Bifurcation at SS65962901 | - | 3 | - | Lev 3 Bifurcation | 0 | 3+ | 0 | 2+ | Good storm & DWF coverage - some erratic depth data | Okay for removal - good data (FM71 d/s for catchment FM) | Removal / Removed
FM60 | CSO at Penlan Crescent (Point 52A) Swansea - 71059 | SOWQAS P2 | 3 | IDP1 | Asset Incoming Flow | No readings beyond 28th August | 3+ | No DWF-storm sewer | 0 | Good storm coverage, poor data during DWF - low flows. | Okay for removal - good storm data, low flows during DWF | Removal / Removed
FM61 | CSO at Penlan Crescent (Point 52A) Swansea - 71059 | SOWQAS P2 | 3 | IDP1 | Asset Continuation Flow | Low flows, adequate velocities, poor depth data | 3+ | 0 | 0 | Aqequate velocity, poor depth - low flows | Remove - poor data, no alternatives | Removal / Removed
FM62 | Swansea Hol Nant Gelli Point 69A - 52510 | SOWQAS P2 | 3 | IDP1 | Asset Incoming Flow | No Flow data for entire survey | 0 | No DWF-spill pipe | 0 | Limited depth data - spill pipe | Okay for removal - depth only | Removal / Removed
FM63 | Swansea Hol Nant Gelli Point 69A - 52510 | SOWQAS P2 | 3 | IDP1 | Asset Continuation Flow | 0 | 3+ | 0 | 2 | Good storm & DWF coverage - good data | Okay for removal | Removal / Removed
FM64 | CSO 69 Twyddfa Road Swansea - 70955 | SOWQAS P2 | 3 | IDP1 | Asset Incoming Flow | 0 | 3+ | 0 | 2 | Velocity data only, poor depths - low flows | Okay for removal - low flows | Removal / Removed
FM65 | CSO 69 Twyddfa Road Swansea - 70955 | SOWQAS P2 | 3 | IDP1 | Asset Incoming Flow | 0 | 3+ | 0 | 2 | Good storm & DWF coverage - good data | Retain for catchment FM - FM58 u/s poor data. Depth only data d/s (FM97/98) | Retain - Catchment FM | No need to have both FM65 and FM66, FM65 has better data so retained | Medium | Good | Possible
FM66 | CSO 69 Twyddfa Road Swansea - 70955 | SOWQAS P2 | 3 | IDP1 | Asset Continuation Flow | 0 | 3+ | 0 | 1 | Good storm & DWF coverage - some velocity data drop-out | Okay for removal - retain FM65 u/s | Removal / Removed
FM67 | CSO 70 A4067 Nthbnd Landore Swansea - 52497 | SOAF (Live) | 3 | None | Asset Incoming Flow 1 | 0 | 3+ | 0 | 2 | Good velocity, erratic depth - storms okay | Relocated to X 10/09 to FM159 - removed | Removal / Removed
FM68 | CSO 70 A4067 Nthbnd Landore Swansea - 52497 | SOAF (Live) | 3 | None | Asset Incoming Flow 2 | 0 | 3+ | 0 | 2 | Good storm & DWF coverage - some erratic depths, high velocities | Erratic data - okay for removal, catchment covered u/s | Removal / Removed
FM69 | CSO 70 A4067 Nthbnd Landore Swansea - 52497 | SOAF (Live) | 3 | None | Asset Continuation Flow | 0 | 3+ | No DWF-located on spill pipe | 0 | Spill pipe - storms picked up | Okay for removal - spill pipe | Removal / Removed
FM70 | BRYNHYFRYD CSO LLANGYFELACH ROAD - 71460 | SOAF (Live) | 3 | None | Asset Incoming Flow | 0 | 3+ | 0 | 0 | Erratic depths, some velocities - recently relocated | Relocated to X 10/09 to FM160 - removed | Removal / Removed
FM71 | BRYNHYFRYD CSO LLANGYFELACH ROAD - 71460 | SOAF (Live) | 3 | None | Asset Continuation Flow | 0 | 3+ | 0 | 2 | Good storm & DWF coverage - good data | Retain for catchment FM (FM68 d/s poor data) | Retain - Catchment FM | Retain, remove FM68 d/s as poor data | Medium | Good | Possible
FM72 | Bifurcation at SS65954801 | - | 3 | - | Lev 3 Bifurcation | 0 | 3+ | No DWF-bifurcation | 0 | Depths and some velocities for storms - bifurcation | Retain for catchment FM - bifurcation (FM68 d/s poor data) | Removal / Removed | Retain, remove FM68 d/s as poor data
FM73 | Bifurcation at SS65954710 | - | 4 | - | Lev 4 Bifurcation | 0 | 3+ | 0 | 0 | Good storm & DWF coverage - some velocity data drop-out | FM at BIF u/s of Cwmbrwla x3 CSOs - to be retained | Retain - Cwmbrwla x3 CSOs BIF |  | Medium | Poor / low | Yes
FM74 | Bifurcation at SS65974710 | - | 4 | - | Lev 4 Bifurcation | 0 | 3+ | 0 | 1 | Velocity data only, poor depths - low flows, BIF | Poor data - to be removed (keep FM77 instead for BIF, better data) | Removal / Removed
FM75 | 48 Eaton St CSO, Swansea - 74695 | UCSO | 4 | IDP2 | Asset Incoming Flow | 0 | 3+ | 0 | 2 | Good storm & DWF coverage - some velocity data drop-out | Good data, UCSO driver (low spiller) - to be removed | Removal / Removed
FM76 | 48 Eaton St CSO, Swansea - 74695 | UCSO | 4 | IDP2 | Asset Incoming Flow | 0 | 3+ | 0 | 2+ | Good storm & DWF coverage - low depths | Good data, UCSO driver (low spiller) - to be removed | Removal / Removed
FM77 | 48 Eaton St CSO, Swansea - 74695 | UCSO | 4 | IDP2 | Asset Continuation Flow | 0 | 3+ | 0 | 0 | Good storm & DWF coverage - good data | FM at BIF u/s of Cwmbrwla x3 CSOs - to be retained (keep instead of FM74, better data) | Retain - Cwmbrwla x3 CSOs BIF |  | Low | Good | Possible
FM78 | Bonymaen Rd CSO - 73040 | SOWQAS P2 | 3 | IDP1 | Asset Incoming Flow | 0 | 3+ | 0 | 2+ | Good storm & DWF coverage - some erratic depths | Okay for removal | Removal / Removed
FM80 | Opp 74 Bonymaen Rd CSO - 70964 | SOWQAS P2 | 3 | IDP1 | Asset Continuation Flow | 0 | 3+ | 0 | 2+ | Good storm & DWF coverage - good data | Okay for removal | Removal / Removed
FM81 | Pentrechwyth Rd CSO - 52462 | SOWQAS P2 | 3 | IDP1 | Asset Incoming Flow | 0 | 3+ | 0 | 2 | Good storm & DWF coverage - good data | Okay for removal - retain FM82 d/s | Removal / Removed | No need to have both FM81 and FM82, FM81 on outgoing pipe and FM82 has better data so retained
FM82 | Pentrechwyth Rd CSO - 52462 | SOWQAS P2 | 3 | IDP1 | Asset Continuation Flow | 0 | 3+ | 0 | 2+ | Good storm & DWF coverage - good data | Okay for removal - good data (FM94 d/s for catchment FM) | Removal / Removed
FM83 | Cwmbrwla Roundabout CSO - 71421 | SOWQAS P2 | 3 | IDP1 | Asset Incoming Flow | 0 | 3+ | 0 | 2+ | Good storm & DWF coverage - some velocity data drop-out | FM around Cwmbrwla x3 CSOs | Retain - Cwmbrwla x3 CSOs |  | Medium | Medium | Possible
FM84 | Cwmbrwla Roundabout CSO - 71421 | SOWQAS P2 | 3 | IDP1 | Asset Continuation Flow | 0 | 3+ | 0 | 2+ | Good storm & DWF coverage - good data | FM around Cwmbrwla x3 CSOs | Retain - Cwmbrwla x3 CSOs |  | High | Good | No
FM85 | CSO 60 Gors Avenue Swansea - 70951 | SOWQAS P2 | 3 | IDP1 | Asset Incoming Flow | 0 | 3+ | 0 | 2 | Good storm & DWF coverage - some velocity drop out, low depths | FM around Cwmbrwla x3 CSOs | Retain - Cwmbrwla x3 CSOs |  | Low | Medium | Possible
FM86 | CSO 60 Gors Avenue Swansea - 70951 | SOWQAS P2 | 3 | IDP1 | Asset Incoming Flow | 0 | 3+ | 0 | 2+ | Good storm & DWF coverage - good data | FM around Cwmbrwla x3 CSOs | Retain - Cwmbrwla x3 CSOs |  | High | Poor | Possible
FM87 | CSO 60 Gors Avenue Swansea - 70951 | SOWQAS P2 | 3 | IDP1 | Asset Continuation Flow | 0 | 3+ | 0 | 2 | Good storm & DWF coverage - some velocity data drop-out | FM around Cwmbrwla x3 CSOs | Retain - Cwmbrwla x3 CSOs |  | High | Medium | Possible
FM88 | CSO 119 Cwm Road Hafod Swansea - 70968 | SOWQAS P2 | 3 | IDP1 | Asset Incoming Flow | 0 | 3+ | 0 | 1 | Good storm & DWF coverage - good data | FM around Cwmbrwla x3 CSOs | Retain - Cwmbrwla x3 CSOs |  | High | Good | No
FM90 | Glanowen Rd CSO - 73328 | UCSO | 4 | IDP2 | Asset Incoming Flow | Very low depths and velocities | 3+ | Very low depths and velocities | 2 | Very low depths, erratic velocities | Hydraulically linked to FM161 which is to be retained to gain more data | Removal / Removed
FM91 | Glanowen Rd CSO - 73328 | UCSO | 4 | IDP2 | Asset Incoming Flow | 0 | 3+ | 0 | 2+ | Good velocity, low and erratic depths | Hydraulically linked to FM161 which is to be retained to gain more data | Removal / Removed
FM92 | Glanowen Rd CSO - 73328 | UCSO | 4 | IDP2 | Asset Continuation Flow | No data until 5th September | 2 | Bifurcation | 0 | Limited data only for 1 week after 05/09 | Relocated 12/09 to FM161 (wrongly installed on storm) - removed | Removal / Removed
FM93 | Glanowen Rd CSO - 73328 | UCSO | 4 | IDP2 | Asset Continuation Flow | Possible secondary leg of bifurcation | 3+ | 0 | 0 | BIF - limited data, some storm response | Hydraulically linked to FM161 which is to be retained to gain more data | Removal / Removed
FM94 | Catchment FM - incoming to main trunk | - | - | - | Catchment | 0 | 3+ | 0 | 2+ | Good storm & DWF coverage - good data | Retain for catchment FM - flows entering trunk to WwTW | Retain - Catchment FM |  | Medium | Good | No
FM95 | Catchment FM - incoming to main trunk | - | - | - | Catchment | 0 | 3+ | 0 | 2+ | Good storm & DWF coverage - good data | Retain for catchment FM - flows entering trunk to WwTW | Retain - Catchment FM |  | Medium | Good | No
FM96 | Catchment - large unmonitored catchment | - | - | - | Catchment | 0 | 3+ | Bifurcation | 1 | Poor data - low depths and no velocities | To be removed - poor data, no alternatives | Removal / Removed
FM97 | Catchment FM - incoming to main trunk | - | - | - | Catchment | Slow flow, velocity regularly drops out | 3+ | 0 | 0 | Depth only - poor/no velocities | Retain for catchment FM - depth only - flows entering trunk to WwTW | Removal / Removed
FM98 | Catchment FM - incoming to main trunk | - | - | - | Catchment | Large periods with no data | 1 | 0 | 1 | Depth only - poor/no velocities | Retain for catchment FM - depth only - flows entering trunk to WwTW | Retain - Catchment FM |  | Low | Medium | Yes
FM99 | Catchment FM - incoming to main trunk | - | - | - | Catchment | 0 | 3+ | 0 | 2+ | Good depths, velocity only for storms | Retain for catchment FM - flows entering trunk to WwTW | Retain - Catchment FM |  | Low | Good | Possible
FM100 | CSO 121 at Sandfields SPS (Outfall 'L') - 51148 | TEN (Not currently in ECS Scope) | 4 (TBC) | IDP2 (TBC) | Asset Incoming Flow | 0 | 3+ | 0 | 2+ | Good storm & DWF coverage - good data | FM around IDP2 asset, TEN - to be retained | Retain - TEN |  | Low | Good | Possible
FM103 | CSO at Brynmor Road, Swansea - 72398 | SOWQAS P1 | 3 | IDP1 | Asset Continuation Flow | Standing water, no DWF velocity | 3+ | 0 | 0 | Poor data - depth only | Okay for removal, use FM108 d/s for catchment FM | Removal / Removed
FM104 | Catchment - large unmonitored catchment | - | - | - | Catchment | 0 | 3+ | 0 | 2+ | Good storm & DWF coverage - good data | Okay for removal - FM147 d/s has better data and covers same catchment | Removal / Removed | See FM147
FM105 | Catchment - large unmonitored catchment | - | - | - | Catchment | 0 | 3+ | 0 | 2+ | Good storm & DWF coverage - low depths | Okay for removal - FM147 d/s has better data and covers same catchment | Removal / Removed | See FM147
FM106 | Singleton Park Point 24 CSO - 52514 | SOWQAS P1 | 3 | IDP1 | Asset Incoming Flow | 0 | 3+ | 0 | 2+ | Good storm & DWF coverage - good data | Okay for removal - good data (FM107 d/s for catchment FM) | Removal / Removed
FM107 | Singleton Park Point 24 CSO - 52514 | SOWQAS P1 | 3 | IDP1 | Asset Continuation Flow | 0 | 3+ | 0 | 2+ | Good storm & DWF coverage - good data | FM at BIF u/s of IDP2 asset, TEN (Knab Rock SPS) - to be retained | Retain - TEN Bifurcation |  | Low | Good | Possible
FM108 | Bifurcation at SS63913801 | - | 4 | - | Lev 4 Bifurcation | 0 | 3+ | 0 | 0 | Depth only, erratic velocities | FM at BIF u/s of IDP2 asset, TEN (Knab Rock SPS) - to be retained | Retain - TEN Bifurcation |  | Low | Good | Possible
FM110 | Furzeland Drive CSO - 72736 | TEN (Not currently in ECS Scope) | 4 (TBC) | IDP2 (TBC) | Asset Incoming Flow | 0 | 3+ | 0 | 2 | Good storm & DWF coverage - good data | FM around IDP2 asset, TEN - to be retained | Removal / Removed
FM111 | Furzeland Drive CSO - 72736 | TEN (Not currently in ECS Scope) | 4 (TBC) | IDP2 (TBC) | Asset Incoming Flow | 0 | 3+ | 0 | 2 | Good storm & DWF coverage - good data | FM around IDP2 asset, TEN - to be retained | Retain - TEN |  | High | Good | No
FM112 | Furzeland Drive CSO - 72736 | TEN (Not currently in ECS Scope) | 4 (TBC) | IDP2 (TBC) | Asset Continuation Flow | 0 | 3+ | 0 | 0 | Erratic depths, good velocities - relocated | Relocated 16/09 to FM162 - removed | Removal / Removed
FM114 | Catchment FM - incoming to main trunk | - | - | - | Catchment | 0 | 3+ | 0 | 2+ | Good storm & DWF coverage - good data | Retain for catchment FM - flows to main trunk to Knab Rock SPS (TEN) | Retain - TEN |  | Low | Good | Possible
FM115 | Catchment - large unmonitored catchment | - | - | - | Catchment | 0 | 3+ | 0 | 2+ | Good storm & DWF coverage - some velocity data drop-out | Retain for catchment FM - flows to main trunk to Knab Rock SPS (TEN) | Retain - TEN |  | Medium | Good | Possible
FM116 | Catchment - large unmonitored catchment | - | - | - | Catchment | 0 | 3+ | 0 | 2+ | Good storm & DWF coverage - quite erratic data | Retain for catchment FM - flows to main trunk to Knab Rock SPS (TEN) | Removal / Removed
FM117 | Storm Overflow at Outfall G via CSO 16 - 52518 | SOWQAS P1 | 3 | IDP1 | Asset Incoming Flow | 0 | 3+ | 0 | 2 | Good storm & DWF coverage - some erratic data | Retain for catchment FM - flows to main trunk to Knab Rock SPS (TEN) | Retain - TEN |  | Low | Poor / low | Yes
FM118 | Storm Overflow at Outfall G via CSO 16 - 52518 | SOWQAS P1 | 3 | IDP1 | Asset Continuation Flow | 0 | 3+ | 0 | 0 | Depth only - poor/no velocities | Retain for catchment FM - depth only on main trunk to Knab Rock SPS (TEN) | Retain - TEN |  | Low | Poor / low | Yes
FM119 | CSO at Fairwood Road, Swansea - 71032 | SOWQAS P1 | 3 | IDP1 | Asset Incoming Flow | 0 | 3+ | 0 | 1 | Good storm & DWF coverage - low depths/flows | Okay for removal - low depths/flows | Removal / Removed
FM120 | CSO at Fairwood Road, Swansea - 71032 | SOWQAS P1 | 3 | IDP1 | Asset Continuation Flow | 0 | 3+ | 0 | 2 | Good storm & DWF coverage - some erratic data | Okay for removal | Removal / Removed
FM121 | Catchment FM - incoming to main trunk | - | - | - | Catchment | 0 | 3+ | 0 | 0 | Good storm & DWF coverage - low depths | Retain for catchment FM - flows to main trunk to Knab Rock SPS (TEN) | Retain - TEN |  | Medium | Medium | Possible
FM122 | Swansea Nr Norton Avenue Point 11 New Ma - 52520 | Non Triggered BW/SFW Asset (20+spills and Lower 8 Dilution) - Likely have high Source Apportionment. | 3 | IDP1 | Asset Incoming Flow 1 | 0 | 2 | 0 | 0 | Good storm & DWF coverage - good data | Okay for removal | Removal / Removed
FM123 | Swansea Nr Norton Avenue Point 11 New Ma - 52520 | Non Triggered BW/SFW Asset (20+spills and Lower 8 Dilution) - Likely have high Source Apportionment. | 3 | IDP1 | Asset Incoming Flow 1 | 0 | 2 | 0 | 0 | Good storm & DWF coverage - some velocity data drop-out | Okay for removal | Removal / Removed
FM124 | Swansea Nr Norton Avenue Point 11 New Ma - 52520 | Non Triggered BW/SFW Asset (20+spills and Lower 8 Dilution) - Likely have high Source Apportionment. | 3 | IDP1 | Asset Continuation Flow | 0 | 3+ | 0 | 2+ | Good storm & DWF coverage - good data | Retain for catchment FM - flows to main trunk to Knab Rock SPS (TEN) | Retain - TEN |  | Medium | Medium | Possible
FM125 | Newton Lady Housty CSO - 51947 | UCSO | 4 | IDP2 | Asset Incoming Flow | Large periods with no data | 0 | 0 | 1 | Large periods with no/missing data - need more data | Need more data, UCSO (hydraulically linked to high spiller 52469) - to be retained | Removal / Removed
FM126 | Newton Lady Housty CSO - 51947 | UCSO | 4 | IDP2 | Asset Continuation Flow | 0 | 3+ | 0 | 2+ | Volume imbalance - to be relocated | Relocated 18/09 to FM163 - removed | Removal / Removed
FM127 | Newton Rd CSO - 52469 | UCSO | 4 | IDP2 | Asset Incoming Flow | 0 | 1 | 0 | 2+ | Generally poor data - some data during Interim 5 - to be relocated | Relocated to spill pipe to FM164 - removed | Removal / Removed
FM128 | Newton Rd CSO - 52469 | UCSO | 4 | IDP2 | Asset Continuation Flow | 0 | 3+ | 0 | 2+ | Good storm & DWF coverage - good data | UCSO (high spiller) - to be retained | Removal / Removed
FM129 | Newton Road (Underhill Park) CSO - 71079 | UCSO | 4 | IDP2 | Asset Incoming Flow | No readings beyond 29th August. Velocity issues during storms | 2 | 0 | 1 | Poor/no velocity data, drifting depths but some storm response | UCSO (hydraulically linked to high spiller 52469) - to be retained | Removal / Removed
FM130 | Newton Road (Underhill Park) CSO - 71079 | UCSO | 4 | IDP2 | Asset Continuation Flow | No readings beyond 29th August. Small US catchment | 3+ | 0 | 1 | Poor data - okay during storms | UCSO (hydraulically linked to high spiller 52469) - to be retained | Removal / Removed
FM131 | MUMBLES SPS KNAB ROCK MUMBLES SWANS - 53153 | TEN (Not currently in ECS Scope) | 4 (TBC) | IDP2 (TBC) | Asset Nearby Incoming Flow to Tunnel 1 | Silt US, slow flow | 0 | 0 | 0 | Depth only, no velocities | FM around IDP2 asset, TEN - to be retained | Removal / Removed
FM132 | MUMBLES SPS KNAB ROCK MUMBLES SWANS - 53153 | TEN (Not currently in ECS Scope) | 4 (TBC) | IDP2 (TBC) | Asset Nearby Incoming Flow to Tunnel 1 | 0 | 3+ | 0 | 2+ | Good storm & DWF coverage - good data | FM around IDP2 asset, TEN - to be retained | Retain - TEN |  | Medium | Good | Possible
FM133 | Bifurcation at SS61886101 | - | 4 | - | Lev 4 Bifurcation | 0 | 3+ | 0 | 2+ | Good storm & DWF coverage - good data | FM at BIF u/s of IDP2 asset, TEN (Knab Rock SPS) - to be retained | Retain - TEN Bifurcation |  | Low | Good | Possible
FM134 | Catchment - large unmonitored catchment | - | - | - | Catchment | 0 | 3+ | 0 | 1 | Good storm & DWF coverage - good data, some large velocity spikes | Incoming flows to Knab Rock SPS | Retain - TEN |  | Low | Good | Possible
FM135 | MUMBLES SPS KNAB ROCK MUMBLES SWANS - 53153 | TEN (Not currently in ECS Scope) | 4 (TBC) | IDP2 (TBC) | Asset Nearby Incoming Flow to Tunnel 2 | high level bifurcation | 3+ | 0 | 1 | BIF - limited data, some storm response | FM around IDP2 asset, TEN - to be retained | Retain - TEN |  | Low | Poor / low | Yes
FM136 | Bifurcation at SS61879801 | - | 4 | - | Lev 4 Bifurcation | Silty slow flows | 0 | 0 | 0 | No velocity data, depth only but quite erratic | To be removed - no alternatives. Other FMs cover incoming flows to Knab Rock SPS | Removal / Removed
FM137 | Bifurcation at SS61879801 | - | 4 | - | Lev 4 Bifurcation | Silty slow flows | 0 | 0 | 0 | Depth only, limited velocity data | To be removed - no alternatives. Other FMs cover incoming flows to Knab Rock SPS | Removal / Removed
FM138 | MUMBLES SPS KNAB ROCK MUMBLES SWANS - 53153 | TEN (Not currently in ECS Scope) | 4 (TBC) | IDP2 (TBC) | Asset Nearby Incoming Flow to Tunnel 1 | 0 | 3+ | 0 | 2 | Good storm & DWF coverage - good data | FM around IDP2 asset, TEN - to be retained | Retain - TEN |  | Low | Medium | Possible
FM139 | Limeslade - 71007 | - | 4 | - | Asset Incoming Flow | 0 | 3+ | 0 | 2 | Good storm & DWF coverage - good data | EO to Storm but also inflow to Knab Rock SPS (TEN) - to be retained | Retain - TEN |  | Low | Medium | Possible
FM140 | CSO and EO at Fabian Way SPS - 53103 | SOWQAS P2 | 3 | IDP1 | Asset Incoming Flow | 0 | 3+ | 0 | 2 | Erratic depths, low flows | To be removed - no alternatives | Removal / Removed
FM141 | CSO 64A PENLANFACH BRYNHYFRYD - 74683 | SOWQAS | 3 | IDP1 | Asset Incoming Flow | Issues with depth | 0 | 0 | 2 | Low flows, erratic depths | To be removed - no alternatives | Removal / Removed
FM142 | CSO 64A PENLANFACH BRYNHYFRYD - 74683 | SOWQAS | 3 | IDP1 | Asset Incoming Flow (Storm) | 0 | 3+ | 0 | 0 | Erratic depths, limited velocities apart from Interim 5 | To be removed - no alternatives | Removal / Removed
FM143 | Hopkin Street Brynhyfryd - 75105 | SOWQAS | 3 | IDP1 | Asset Incoming Flow | 0 | 3 | 0 | 1 | Erratic depths, velocities okay | To be removed - no alternatives | Removal / Removed
FM144 | Rear of 50 Hopkin Street | SOWQAS | 3 | IDP1 | Asset Continuation Flow | 0 | 3+ | 0 | 0 | Good storm & DWF coverage - good data | Okay for removal - good data | Removal / Removed
FM145 | Hopkin Street Brynhyfryd - 75105 | SOWQAS | 3 | IDP1 | Asset Incoming Flow (Storm) | Large periods with no data | 3 | located on storm pipe | 0 | Generally poor data - some velocity data during early interims | To be removed - no alternatives | Removal / Removed
FM146 | Rear of 50 Hopkin Street | SOWQAS | 3 | IDP1 | Asset Continuation Flow (Storm) | 0 | 3+ | 0 | 2 | Good storm & DWF coverage - good data | Okay for removal - good data | Removal / Removed
FM147 | Singleton Park Point 24 CSO - 52514 | SOWQAS P1 | 3 | IDP1 | Asset Incoming Flow | 0 | 3+ | 0 | 2+ | Good storm & DWF coverage - good data | Okay for removal - good data (FM107 d/s for catchment FM) | Removal / Removed | Retain FM147 as catchment FM, FM104 and FM105 u/s have poorer data and cover same catchment
FM148 | CSO at Penlan Crescent (Point 52A) Swansea - 71059 | SOWQAS P2 | 3 | IDP1 | Asset Spill Flow - Storm System | 0 | 3+ | 0 | 1 | Velocity okay, erratic depths - okay during storms | To be removed - no alternatives | Removal / Removed
FM149 | Catchment - incoming to main trunk | - | - | - | Catchment | 0 | 3+ | 0 | 2 | Good storm & DWF coverage - good data | Retain for catchment FM - flows entering trunk to WwTW | Retain - Catchment FM |  | Low | Medium | Possible
FM150 | Catchment - large unmonitored catchment | - | - | - | Catchment | 0 | 3+ | 0 | 0 | Erratic and low depths, no velocity data | To be removed - no alternatives | Removal / Removed
FM151 | Cwmbrwla Roundabout CSO - 71421 | SOWQAS P2 | 3 | IDP1 | Asset Incoming Flow | 0 | 3+ | 0 | 2+ | Good storm & DWF coverage - good data | FM around Cwmbrwla x3 CSOs | Retain - Cwmbrwla x3 CSOs |  | Medium | Good | No
FM152 | Cwmbrwla Roundabout CSO - 71421 | SOWQAS P2 | 3 | IDP1 | Asset Incoming Flow | 0 | 3+ | 0 | 2+ | Good storm & DWF coverage - good data | FM around Cwmbrwla x3 CSOs | Retain - Cwmbrwla x3 CSOs |  | Medium | Good | No
FM153 | Cwmbrwla Roundabout CSO - 71421 | SOWQAS P2 | 3 | IDP1 | Asset Incoming Flow | 0 | 0 | 0 | 1 | Erratic data, only data from 29/08 - installed late | FM around Cwmbrwla x3 CSOs | Retain - Cwmbrwla x3 CSOs |  | Low | Medium | Possible
FM154 | Cwmbrwla Roundabout CSO - 71421 | SOWQAS P2 | 3 | IDP1 | Asset Incoming Flow | 0 | 0 | 0 | 2 | Good data, only data from 29/08 - installed late | FM around Cwmbrwla x3 CSOs | Retain - Cwmbrwla x3 CSOs |  | High | Good | No
FM155 | Heol Y Nant/Sybil Street Clydach CSO - 70975 | SOWQAS P2 | 3 | IDP1 | [6 empty] | Installed 20/09 - relocation of FM06. IDP2 asset d/s, hydraulically linked to SO IMP1 - to be retained | Retain - linked to SO IMP1 asset d/s |  | Medium | Good | Possible
FM156 | No6 Heol Dyfan CSO, Morriston - 70961 | UCSO | 4 | IDP2 | [5 empty] | Installed 03/09 - relocation of FM32, shows improvement, need more data | Relocation shows improvement in data, retain to gain more data | Removal / Removed
FM157 | CSO 80 Pentrpoeth Rd Morriston - 70959 | SOWQAS P2 | 3 | IDP1 | [5 empty] | Installed 19/09 - relocation of FM34, no data provided since relocation, need more data | No data since relocation, need more data. FM158 nearby also to be retained. | Removal / Removed
FM158 | CSO 80 Pentrpoeth Rd Morriston - 70959 | SOWQAS P2 | 3 | IDP1 | [5 empty] | Installed 10/09 - relocation of FM35, shows improvement, need more data | Relocation shows improvement in data, retain to gain more data. FM157 nearby also to be retained. | Removal / Removed
FM159 | CSO 70 A4067 Nthbnd Landore Swansea - 52497 | SOAF (Live) | 3 | None | [5 empty] | Installed 10/09 - relocation of FM67, no improvement in data quality | Poor data after relocation - to be removed | Removal / Removed
FM160 | BRYNHYFRYD CSO LLANGYFELACH ROAD - 71460 | SOAF (Live) | 3 | None | [5 empty] | Installed 10/09 - relocation of FM70, no improvement in data quality | Poor data after relocation - to be removed | Removal / Removed
FM161 | Glanowen Rd CSO - 73328 | UCSO | 4 | IDP2 | [5 empty] | Installed 12/09 - not enough data to determine data quality since relocation, need more data | Not enough data since relocation, need more data | Removal / Removed
FM162 | Furzeland Drive CSO - 72736 | TEN (Not currently in ECS Scope) | 4 (TBC) | IDP2 (TBC) | [6 empty] | Installed 16/09 - relocation of FM112. FM around IDP2 asset, TEN - to be retained | Removal / Removed
FM163 | Newton Lady Housty CSO - 51947 | UCSO | 4 | IDP2 | [6 empty] | Installed 18/09 - relocation of FM126. UCSO (hydraulically linked to high spiller 52469) - to be retained | Removal / Removed
FM164 | Newton Rd CSO - 52469 | UCSO | 4 | IDP2 | [6 empty] | Installed 05/09 - relocation of FM127. UCSO (high spiller) - to be retained | Removal / Removed
FM165 | Storm Overflow at Outfall G via CSO 16 - 52518 | SOWQAS P1 | 3 | IDP1 | Asset Incoming Flow | #N/A | #N/A | #N/A | #N/A |  | Retain for catchment FM - flows to main trunk to Knab Rock SPS (TEN) | Retain - TEN |  | Medium | Good | Possible
FM166 | Storm Overflow at Outfall G via CSO 16 - 52518 | SOWQAS P1 | 3 | IDP1 | Asset Continuation Flow | #N/A | #N/A | #N/A | #N/A |  | Retain for catchment FM - depth only on main trunk to Knab Rock SPS (TEN) | Retain - TEN |  | Medium | Good | Possible
DM01 | Furzeland Drive CSO - 72736 | TEN (Not currently in ECS Scope) | 4 (TBC) | IDP2 (TBC) | Storm Tank | 0 | 0 | 0 | 0 | Good data - depth response during storms | FM around IDP2 asset, TEN - to be retained | Retain - TEN
DM02 | Temporary Increased Dis. From - 50918 | EO to Storm | 4 | IDP2 | Pumping Station Wet Well | 0 | 0 | 0 | 0 | Good data - only upto 27/08, need more data | No budget for EO to Storm, to be removed | Removal / Removed
DM03 | Baldwins Crescent SPS - 50834 | EO to Storm | 4 | IDP2 | Pumping Station Wet Well - RISK OF DANGEROUS GASSES | 0 | 0 | 0 | 0 | Mostly good data - some drop outs and erratic interim 4/5 | No budget for EO to Storm, to be removed | Removal / Removed
PL01 | Glais CSO / Glais SPS - 50944 | SOWQAS P2 | 3 | IDP1 | Asset Continuation Flow | 0 | 0 | 0 | 0 |  | IDP2 asset u/s, UCSO (low spiller) - to be removed | Removal / Removed
PL02 | DRUMAU FARM BIRCHGROVE RD P.S. CSO - 52447 | SOAF (Live) | 3 | None | Asset Continuation Flow | 0 | 0 | 0 | 0 |  | Okay for removal - check data | Removal / Removed
PL03 | CSO Halfway Crymlyn Road PS - 50961 | SOWQAS P2 | 3 | IDP1 | Asset Continuation Flow | 0 | 0 | 0 | 0 |  | FM37 to be removed u/s - okay for removal | Removal / Removed
PL04 | Catchment Split - Fendrod SPS - 70010 | - | - | - | Asset Continuation Flow | 0 | 0 | 0 | 0 |  | Key catchment SPS - retain | Retain - Catchment FM
PL05 | Mumbles SPS Knab Rock Mumbles Swans - 53153 | TEN (Not currently in ECS Scope) | 4 (TBC) | IDP2 (TBC) | Asset Continuation Flow | 0 | 0 | 0 | 0 |  | FM around IDP2 asset, TEN - to be retained | Retain - TEN
PL06 | Limeslade - 71007 | EO to Storm | 4 | IDP2 | Asset Continuation Flow | 0 | 0 | 0 | 0 |  | EO to Storm but also inflow to Knab Rock SPS (TEN) - to be retained | Retain - TEN
PL07 | CSO and EO at Fabian Way SPS - 53103 | SOWQAS P2 | 3 | IDP1 | Asset Continuation Flow | 0 | 0 | 0 | 0 |  | FM140 to be removed u/s - okay for removal | Removal / Removed
PL08 | Temporary Increased Dis. From - 50918 | EO to Storm | 4 | IDP2 | Asset Continuation Flow | 0 | 0 | 0 | 0 |  | No budget for EO to Storm, to be removed | Removal / Removed
PL09 | Baldwins Crescent SPS - 50834 | EO to Storm | 4 | IDP2 | Asset Continuation Flow - RISK OF DANGEROUS GASSES | 0 | 0 | 0 | 0 |  | No budget for EO to Storm, to be removed | Removal / Removed

## DryDays compliance
Storm Events
To ensure project success check that each monitor recorded satisfactory data during each storm event. This sheet allows an audit trail into the reasons why the flow survey was removed. If sufficient data was not recorded then why was the flow survey removed?
No Flow = depth data but not velocity or flow
No data = no depth or velocity
|  |  | 2024-09-04 |  |  | No DWF = spill pipe, high level bifurcation etc
FM / DM / PL | Dry Day 1 | Dry Day 2 | Dry Day 3 | COMMENT | Dry Event Coverage (Not exclusive to events state to the left)
| COMMENT | COMMENT | COMMENT
FM01 | Poor data.Velocity data spiky. | N - Poor data | N - Poor Data |  | 0
FM02 | Y - | Y - | Y - |  | 2+ | Add in comment when no DWF expected e.g. high level bifurcation, spill pipe
FM03 | Y - | N-no data | N - No Data | Very Low Flow in DWF | 1 | Negative depth | ingore for now flaged
FM04 | Y - | Y - | Y - Small spike, possible rainfall |  | 2+ | Very low flows
FM05 | Bifurcation-No DWF | Bifurcation.No DWF | N - No Flow | No DWF-bifurcation | 0 | Should we check each week
FM06 | Y - | N - no data | N - No Flow |  | 1
FM09 | Y - | N - no data | N - No Data |  | 1 | on comment column, if no dry days, check other dry days to see if consistent
FM10 | Y - | Y - | N - No Data |  | 2 | add column to say if okay for removal
FM11 | No DWF | N-No DWF | N - No Data | No DWF-high level bifurcation | 0
FM13 | No diruranl profile | N - No Data | N - No Data |  | 0
FM14 | No data | N - No Data | N - No Data | No DWF-Small upstream catchment | 0
FM15 | No data | N - No Data | N - No Data |  | 0
FM16 | Y - | Y - | Y - Very Low Flows |  | 2+
FM17 | Poor data.Velocity drop out | N - Poor data.Data drops out | N - No Flow |  | 0
FM18 | Located on spill pipe .No flow on DWF | N - Located on spill pipe. | N - No Data | No DWF-located on spill pipe | 0
FM19 | Y - | Y - | Y - | Small upstream catchment | 0
FM20 | No velocity data | N - Poor data.Negative depth values. | N - No Data |  | 0
FM21 | Y - | Y - | Y - |  | 2+
FM22 | Poor data.Velocity drop out | N - Poor data.Velocity drop out. | N - No Data |  | 0
FM23 | Y - | Y - | N - No Data |  | 2
FM24 | Y.Very low DWF | Y-low DWF | N - No Data | Small upstream catchment | 2
FM25 | Y - | N - negative depth values | N - No Data |  | 1
FM26 | Y - | Y - | N - No Data |  | 2
FM27 | Y - | Y - | Y - Very Low Flows |  | 2+
FM28 | Y - | Y - | N - No Data |  | 2
FM29 | Y.Drop in velocity data | Y - | Y - Small spike, possible rainfall |  | 2+
FM30 | Y | Y - | N - No Data |  | 1
FM31 | Very low DWF.Small upstream catchment. | N - no data | N - No Data | Small u/s catchment | 0
FM32 | Low DWF.Negative depth values | Low DWF.Negative depth values | N - No Data |  | 0
FM33 | No DWF.Located on spill pipe | N - no data | N - No Data | No DWF-located on spill pipe | 0
FM34 | Poor data.Velocity drop out | N - negative depth values | N - No Flow |  | 0
FM35 | Y - | Y - | N - No Data |  | 2
FM37 | Y - | Y - | Y - |  | 2+
FM38 | Y - | Y - | N - No Data |  | 2
FM39 | Y - | N - no data | N - No Flow |  | 1
FM40 | Y - | Y - | N - No Data |  | 2
FM41 | Y - | Y - | N - No Data |  | 2
FM42 | Y - | Y - | Y - |  | 0
FM43 | Poor data | N - no data | N - No Flow |  | 0
FM44 | Poor data .Velocity drop out | Y - | Y - |  | 2
FM45 | Y - | Y - | Y - |  | 2+
FM47 | Poor data .No velocity recorded. | N - no flow | N - No Flow |  | 0
FM48 | Y - Very low flow | N - negative depth values | N - No Flow |  | 1
FM49 | Y - | Y - | N - No Data |  | 2
FM50 | No data | No data | N - No Data |  | 0
FM51 | Gap in data | Gap in data | Y - No flow until ~8am |  | 1
FM54 | Located on spill pipe.No DWF | No DWF.Located on spill pipe | N - No Flow | No DWF-located on spill pipe | 0
FM55 | Y - Very low DWF due to small u/s catchment | Y - | N - No Data |  | 2
FM56 | Y - | N-no velocuty data at the start | Y - Very Low Flows |  | 2
FM57 | Few velocity drop outs. | Y - | Y - Very Low Flows |  | 2
FM58 | No flow.FM located on bifurcation | No DWF(bifurcation) | N - No Data | No DWF-bifurcation | 0
FM59 | Y - | Y - | Y - Very Low Flows |  | 2+
FM60 | No DWF.Storm sewer | No DWF.Storm sewer | N - No Data | No DWF-storm sewer | 0
FM61 | Poor data | No data | N - No Data |  | 0
FM62 | Spill pipe-No DWF | Spill pipe-No DWF | N - No Data | No DWF-spill pipe | 0
FM63 | Y - | Y - | N - No Data |  | 2
FM64 | Y - | Y - | N - No Data |  | 2
FM65 | Y - | Y - | N - No Data |  | 2
FM66 | Velocity drop out | No data | Y - Very Low Flows |  | 1
FM67 | Y - | Y - | N - No Data |  | 2
FM68 | Y - | N-poor data.Negative depth values.Velocity drops down | Y - |  | 2
FM69 | No DWF.Spill pipe | No DWF-spill pipe | N - No Data | No DWF-located on spill pipe | 0
FM70 | No velocity data | N-No velocity data | N - No Data |  | 0
FM71 | Y - | Y - | N - No Data |  | 2
FM72 | Bifurcation-No DWF | No DWF-bifurcation | N - No Data | No DWF-bifurcation | 0
FM73 | Poor data | Poor data | N - No Data |  | 0
FM74 | Y - | N-velocity drop out | N - No Flow |  | 1
FM75 | Y - | Y - | N - No Data |  | 2
FM76 | Y - | Y - | Y - Very Low Flows |  | 2+
FM77 | Y - | Y - | N - No Data
FM78 | Y - | Y - | Y - Very Low Flows |  | 2+
FM80 | Y - | Y - | Y - Very Low Flows |  | 2+
FM81 | Y - | Y - | N - No Data |  | 2
FM82 | Y - | Y - | Y - |  | 2+
FM83 | Y - | Y - | Y - Very Low Flows |  | 2+
FM84 | Y - | Y - | Y - |  | 2+
FM85 | Y - | N-No data | Y - Very Low Flows |  | 2
FM86 | Y - | Y - | Y - Very Low Flows |  | 2+
FM87 | Y - | N-poor data.Velocity drop out | Y - Very Low Flows |  | 2
FM88 | Y.High velocity values | Y - High velocity values | N - No Data |  | 1
FM90 | Y - low depths | Y - low depths | Y - low depths | Very low depths and velocities | 2
FM91 | Y - | Y - | Y - Very Low Flows |  | 2+
FM92 | No data | N - No Data | N - No Data | Bifurcation | 0
FM93 | N- poor data | N-poor data | N - No Flow |  | 0
FM94 | Y - | Y - | Y - Very Low Flows |  | 2+
FM95 | Y - | Y - | Y - |  | 2+
FM96 | Poor data | Y - | N - No Flow | Bifurcation | 1
FM97 | No data | N-poor data | N - No flow until ~12pm |  | 0
FM98 | Poor data | No data | Y - Very Low Flows |  | 1
FM99 | Y - | Y - | Y - Very Low Flows |  | 2+
FM100 | Y - | Y - | Y - |  | 2+
FM103 | No velocities recorded | N-poor data | N - No Flow |  | 0
FM104 | Y - | Y - | Y - Small spike, possible rainfall |  | 2+
FM105 | Y - | Y - | Y - Very Low Flows |  | 2+
FM106 | Y - | Y - | Y - Very Low Flows |  | 2+
FM107 | Y - | Y - | Y - Very Low Flows |  | 2+
FM108 | N-poor velocity data | N-poor velocity data | N - No Flow |  | 0
FM110 | Y - | Y - high velocity data | N - Data Gap |  | 2
FM111 | Y - | N-no data recorded at starting | Y - |  | 2
FM112 | Poor data | N-poor data | N - Data Gap |  | 0
FM114 | Y - | Y - | Y - |  | 2+
FM115 | Y - | Y - | Y - |  | 2+
FM116 | Y - | Y - | Y - Very Low Flows |  | 2+
FM117 | Y - | Y - | N - No Data |  | 2
FM118 | N- no velocity recorded | N-no velocity data recorded at start | N - No Flow |  | 0
FM119 | N-Negative depth values | N- negative depth values | Y - Very Low Flows |  | 1
FM120 | Y - | Y - | N - No Data |  | 2
FM121 | Very low DWF | Very low DWF | N - No Flow |  | 0
FM122 | Y - | Y - | Y - |  | 0
FM123 | Y - | Y - | Y - |  | 0
FM124 | Y - | Y - | Y - |  | 2+
FM125 | N-no velocity recorded | N-no velocity recorded | Y - Very Low Flows |  | 1
FM126 | Y - | Y - | Y - Very Low Flows |  | 2+
FM127 | Y - | Y - | Y - Very Low Flows |  | 2+
FM128 | Y - | Y - | Y - Small spike, possible rainfall |  | 2+
FM129 | Y - | N- no data | N - No Data |  | 1
FM130 | Y - | N- no data | N - No Data |  | 1
FM131 | No data | N-poor data | N - No Flow |  | 0
FM132 | Y - | Y - | Y - |  | 2+
FM133 | Y - | Y - | Y - Very Low Flows |  | 2+
FM134 | Poor data.Velocity data spiky. | Poor data.Velocity data spiky. | Y - |  | 1
FM135 | No data | Y - | N - No Data |  | 1
FM136 | N-poor data | N-no data | N - No Flow |  | 0
FM137 | N-poor data | N-no data | N - No Flow |  | 0
FM138 | Y - | N-no data | Y - Very Low Flows |  | 2
FM139 | Y - | Y - | N - No Data |  | 2
FM140 | Y - | Y - | N - No Data |  | 2
FM141 | Y - | Y - | N - No Data |  | 2
FM142 | N-poor data | N-poor data.No data recorded at the starting | N - No Data |  | 0
FM143 | Y - | Velocity drops out multiple times | N - No Data |  | 1
FM144 | Velocity drops down at multiple times | Velocity drops out multiple times | N - No Data |  | 0
FM145 | Poor data | N-poor data | N - No Data | located on storm pipe | 0
FM146 | Y - | Y - | N - No Data |  | 2
FM147 | Y - | Y - | Y - Very Low Flows |  | 2+
FM148 | N-negative depth data | Y - | N - No Flow |  | 1
FM149 | Y - | Y - | N - No Data |  | 2
FM150 | poor data | Poor data | N - No Flow |  | 0
FM151 | Y - | Y - | Y - Very Low Flows |  | 2+
FM152 | Y - | Y - | Y - Very Low Flows |  | 2+
FM153 | No data | N-poor data. | Y - Very Low Flows |  | 1
FM154 | No data | Y - | Y - |  | 2
FM155
FM156
FM157
FM158
FM159
FM160
FM161
FM162
FM163
FM164
DM01
DM02
DM03
PL01
PL02
PL03
PL04
PL05
PL06
PL07
PL08
PL09

## Sheet2 (hidden)
FM Number | MH ( MODEL) | Install Date |  | Calibrate data to X pipe size?
FM01 | SJ41691603 | 2020-10-06 | US | 900
FM02 | SJ40686008 | 2020-10-02 | US | 450
FM03 | SJ40679502 | 2020-09-30 | US | 1000
FM04 | SJ40679502 | 2020-09-30 | US | 750
FM05 | SJ40679502 | 2020-09-30 | US | 300
FM06 | SJ40681001 | 2020-10-20 | DS | 1000
FM08 | SJ40683301 | 2020-10-31 | US | 525
FM09 | SJ40686008 | 2020-10-02 | US | 750
FM10 | SJ40693201 | 2020-10-31 | US | 300
FM100 | SJ40665303 | 2020-10-02 | DS | 750
FM101 | SJ40679901 | 2020-10-22 | US | 225
FM102 | SJ38689301 | 2020-09-28 | US | 300
FM103 | SJ40684205 | 2020-10-06 | US | 900
FM104 | Inlet Ch 2 | 2020-09-29 | ?
FM105 | Inlet Ch 1 | 2020-09-29 | ?
FM107 | SJ40677407 | 2020-10-05 | US | 600
FM108 | SJ40684270 | 2020-09-25 | US | 525
FM109 | SJ40686006 | 2020-10-02 | US | 1150
FM11 | SJ41678210 | 2020-10-02 | US | 450
FM110 | SJ41682405 | 2020-10-07 | US | 900
FM111 | SJ41671116 | 2020-10-01 | US | 920 x 600E
FM112 | SJ41671113 | 2020-10-05 | US | 1000
FM113 | SJ40651404 | 2020-09-23 | US | 450
FM114 | SJ34631601 | 2020-09-28 | US | 450
FM115 | SJ33625002 | 2020-10-20 | DS | 450
FM117 | SJ33626002 | 2020-10-06 | US | 300
FM118 | SJ33635401 | 2020-09-29 | US | 375
FM119 | SJ34635934 | 2020-09-24 | US | 600
FM12 | SJ41681305 | 2020-10-01 | US | 675
FM120 | SJ34645196 | 2020-09-25 | US | 225
FM121 | SJ34645196 | 2020-09-25 | US | 600
FM122 | SJ35646305 | 2020-09-28 | US | 225
FM123 | SJ35648503 | 2020-10-20 | US | 750
FM124 | SJ38656104 | 2020-09-24 | US
FM125 | SJ38656003 | 2020-09-23 | DS | 300
FM126 | SJ38659101 | 2020-10-23 | DS
FM127 | SJ37623203 | 2020-09-29 | US | 300
FM128 | SJ38633802 | 2020-09-30 | DS | 1125
FM129 | SJ38641201 | 2020-10-08 | US | 675
FM13 | SJ41681503 | 2020-10-02 | US | 375
FM130 | Sandy Lane Saltney Inlet MH 1 | 2020-09-29 | DS | 450
FM131 | SJ37648510 | 2020-09-29 | US | 450
FM132 | SJ38644001 | 2020-09-28 | us | 675
FM133 | SJ38647902 | 2020-09-23 | us | 225
FM134 | SJ38639901 | 2020-09-28 |  | 225
FM135 | SJ35647401 | 2020-10-21 | us
FM136 | SJ37648904 | 2020-10-08 | DS
FM14 | SJ41683403 | 2020-10-07 | DS | 450
FM140 | SJ40656601 | 2020-09-24 | DS | 300
FM141 | SJ40683113 | 2020-10-13 | Inc
FM15 | SJ41690204 | 2020-10-01 | US | 300
FM16 | SJ42660901 | 2020-09-30 | DS | 525
FM17 | SJ42661803 | 2020-10-02 | US | 560x1000
FM18 | SJ42661801 | 2020-10-07 | US | 1000x500sq
FM19 | SJ42667704 | 2020-09-30 | US | 825
FM20 | SJ42669906 | 2020-09-30 | DS | 450
FM21 | SJ42674201 | 2020-09-30 | Inc | 450
FM22 | SJ45672002 | 2020-10-02 | US | 225
FM23 | SJ40651202 | 2020-09-24 | US | 150
FM24 | SJ40651405_WEIRDUM | 2020-10-16 | US | 300
FM25 | SJ40651401 | 2020-09-24 | US | 450
FM26 | SJ40651410 | 2020-09-24 | US | 450
FM27a | SJ40653401 | 2020-09-24 | US | 675
FM27b | SJ40656501 | 2020-09-24 | US | 450
FM28 | SJ40657703 | 2020-09-23 | US | 450
FM29 | SJ40651301 | 2020-09-23 | DS | 300
FM30 | SJ40657403 | 2020-09-29 | US | 450
FM31 | SJ40656693 | 2020-09-24 | DS | 450
FM32 | SJ40658210 | 2020-10-01 | us | 900
FM33 | SJ40658604 | 2020-09-30 | US | 375
FM34 | SJ40659406fv | 2020-09-30 | DS | 825
FM35 | SJ42650105 | 2020-10-06 | us | 300
FM36 | SJ41664301 | 2020-10-02 | US | 600
FM37 | SJ40653801 | 2020-10-30 | US | 600
FM38 | SJ40656808 | 2020-09-30 | US | 600
FM39 | SJ40656807 | 2020-09-30 | DS | 600
FM40 | SJ40661203 | 2020-10-08 | DS | 690
FM41 | SJ40661104 | 2020-10-16 | DS | 1200
FM42 | SJ40668001 | 2020-10-23 | US
FM43 | SJ41663212 | 2020-09-30 | US | 810
FM44 | SJ41663508 | 2020-10-08 | DS | 600
FM45 | SJ40669802 | 2020-10-01 | US
FM46 | SJ40679001 | 2020-10-01 | DS | 525
FM47 | SJ41661615 | 2020-10-07 | DS | 975
FM48 | SJ41662801 | 2020-10-01 | US | 525
FM49 | Seahill_04 | 2020-09-29 | US | 375
FM50 | SJ36691804 | 2020-09-28 | US
FM50a | SJ36691808 | 2020-11-16 | US | 525
FM51 | SJ36692501 | 2020-09-28 | US | 600
FM52 | SJ36692550 | 2020-09-28 | US | 375
FM53 | SJ36692504 | 2020-09-28 | DS | 825
FM54 | SJ37674607 | 2020-09-28 | US | 450
FM55 | SJ37674604 | 2020-09-28 | US | 375
FM56 | SJ38670122 | 2020-09-28 | DS
FM57 | SJ38674204 | 2020-10-02 | US | 375
FM58 | SJ38674204 | 2020-10-02 | US | 450
FM59 | SJ39670701 | 2020-10-02 | DS | 675
FM60 | SJ39681401 | 2020-10-05 | US | 300
FM61 | SJ43656601 | 2020-10-07 | US | 450
FM62 | SJ41662101 | 2020-09-30 | US | 825
FM63 | SJ41659987 | 2020-09-30 | US | 675
FM64 | JUNC_50909693 | 2020-09-30 | US | 225
FM67 | SJ42640904 | 2020-09-30 | US | 225
FM68 | SJ42640904 | 2020-09-30 | US | 225
FM69 | JUNC_50909693 | 2020-09-30 | US | 225
FM70 | SJ42650918 | 2020-09-30 | US | 900
FM71 | SJ42650920_dummy2 | 2020-09-23 | US | 600
FM72 | SJ42650920 | 2020-09-23 | US | 450
FM74 | SJ42661205 | 2020-10-22 | DS | 450
FM75 | SJ42665102 | 2020-10-09 | US | 300
FM76 | SJ38669402 | 2020-10-01 | US | 900
FM77 | SJ39662701 | 2020-09-29 | US | 1200
FM78 | SJ39678408 | 2020-10-07 | ds | 800
FM79 | SJ39678404 | 2020-10-14 |  | 1200
FM80 | SJ39679712 | 2020-10-21 | DS
FM81 | SJ39679707fv | 2020-10-01 | DS | 600
FM82 | SJ41693501 | 2020-10-08 | US | 225
FM83 | SJ41694404 | 2020-10-01 | US | 375
FM84 | SJ41682101 | 2020-09-30 | US | 300
FM85 | SJ42645101 | 2020-10-21 | DS | 225
FM86 | SJ40669001 | 2020-10-01 | US | 1000
FM87 | SJ40653601 | 2020-10-01 | us | 1200
FM88 | SJ40655601 | 2020-10-07 | US
FM89 | SJ39668503 | 2020-09-28 | US | 1175
FM90 | SJ39677307 | 2020-10-05 | US | 825
FM91 | SJ41652302 | 2020-09-28 |  | 300
FM92 | SJ42655703 | 2020-10-01 | US | 225
FM93 | SJ41679602 | 2020-10-01 | US | 225
FM94 | SJ41674401 | 2020-10-01 | US | 225
FM95 | SJ41693501 | 2020-10-13 | US | 225
FM96 | SJ36693803 | 2020-10-07 | DS | 150
FM97 | SJ36702201 | 2020-09-28 | US | 225
FM98 | SJ41662804 | 2020-10-01 | US | 1000
FM99 | SJ41671111 | 2020-10-01 | US | 450
DM01
DM02
DM03
DM04
DM05 |  | 2020-09-30
DM06 |  | 2020-09-30
DM07 |  | 2020-09-29
DM08 |  | 2020-09-29
DM09 |  | 2020-09-29
DM10 |  | 2020-09-29
DM11
DM12
DM13
DM14
DM15 |  | 2020-09-29
DM16 |  | 2020-09-29
DM17 |  | 2020-09-29
DM18 |  | 2020-10-20